## Sheet1
Primary Incident Classification | Wastewater Treatment Plants
Incident Primary Impact Area | (Multiple Items)
Impact Area | All
Date | Incident ID | Location Description | Incident Detailed Description | Primary Incident Classification | Incident Date Time | Incident Count
2010-2011 | INC-0010907 | Port Augusta West WWTP | New gate at Lake Dempsey forced open to gain access. Tyre track visable. No other damage | Type 3 | 2010-08-25 15:05:00 | 1
2012-2013 | INC-0028217 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Transport delivery truck damaging the autosampler shed while leaving the Port Pirie WWTP. The driver has made a SA Water Empolyee aware of the damaged. | Type 3 | 2013-06-07 13:22:00 | 1
2014-2015 | INC-0001052 | Aldinga WWTP | Microcystis flos-aquae 17,300 cells/mL detected @ SP 41805 Aldinga WWTP Lagoon 1 | Type 2 | 2015-04-21 17:31:00 | 1
2014-2015 | INC-0005341 | Christies Beach WWTP | Wastewater overflow from Inspection Point into side entry pit then into Dry Creek system | Type 2 | 2014-07-02 15:50:00 | 1
2014-2015 | INC-0013687 | Christies Beach WWTP | E.coli 520 /100mL detected at SP4101 Christies Beach WWTP Final Effluent AC on : 11/02/2015 12:00:00 AM System: Christies Beach WWTP Zone: Christies Beach (WWTP) | Type 2 | 2015-02-13 09:30:00 | 1
2014-2015 | INC-0015381 | Christies Beach WWTP | Failure of A/B plant PLC at 5:19am shutdown the Chlorine dosing system resulting in the continual release of un-disinfected effluent for >1hr (1hr 56min). The Process Technician was alerted to a Network 1 fault at 5:39am, he immediately logged into the plant SCADA however was unable to understand operational status of A/B plant due to a loss of communication. He then attended site arriving at 7:00am at which point became aware that the A/B plant PLC had failed and the Chlorine disinfection system had shutdown. | Type 1 | 2015-06-23 15:01:00 | 1
2014-2015 | INC-0020496 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2014-2015 | INC-0020652 | Christies Beach WWTP | Operator received a SCADA alarm notification at 6.10am alerting him to a .21NTU 24hr average on membrane train 4, exceeding the type 2 limit of >.2NTU Upon investigation at 7:50am it became apparent that train 4 had run continuously from 19:38 to 02:03 at >.5NTU without generating a SCADA alarm. | Type 1 | 2015-03-18 09:50:00 | 1
2014-2015 | INC-0028920 | Glenelg Waste Water Treatment Plant | Scheduled manual pump down of the Glenelg main pump station caused the inlet screens to overflow, this resulted in 3-4Kl of screened sewage leaving the site and entering the Patawalonga River via the local storm water system on Anderson Ave. | Type 1 | 2014-12-11 16:27:00 | 1
2014-2015 | INC-0029695 | Aldinga WWTP | E.coli 1700 /100mL detected at SP41938 Aldinga WWTP - Final Effluent AC on 17/06/2015 12:00:00 AM System: Aldinga WWTP Zone: Aldinga WWTP | Type 1 | 2015-06-18 13:15:00 | 1
2014-2015 | INC-0032790 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2015-2016 | INC-0001107 | Glenelg Waste Water Treatment Plant | Power failure at Glenelg Wastewater Treatment Plant resulting in failure of chlorination system for greater than one hour. | Type 1 | 2015-09-06 22:38:00 | 1
2015-2016 | INC-0014006 | Christies Beach WWTP | Rotation of duty pump due to backwash valve fault, resulted in a high turbidity automatic shutdown of C plant membrane train 6 (>.2NTU). | Type 2 | 2015-12-15 09:53:00 | 1
2015-2016 | INC-0015772 | Port Lincoln WWTP | There was a disruption to supply of re-use water to Pt Lincoln Council due to a contractor striking the main, no contact was made to PL WWTP operator, other than by PL Council. | Type 3 | 2015-08-05 13:46:00 | 1
2015-2016 | INC-0020603 | Christies Beach WWTP | Restart of membrane train #3 at 13.10 today after being offline overnight saw a recorded value of 1.02NTU and control shutdown train at 13.15. | Type 2 | 2015-11-24 08:10:00 | 1
2015-2016 | INC-0022807 | Glenelg Waste Water Treatment Plant | Commissioning of the Glenelg main pump station caused surging in the pumping main resulting inlet screens to overflow, this resulted in 144kl of screened sewage leaving the site and entering the Patawalonga River via the local storm water system on Anderson Ave. | Type 1 | 2016-03-04 12:04:00 | 1
2016-2017 | INC-0001523 | Glenelg Waste Water Treatment Plant | E.coli 920 MPN/100mL detected at SP40556 Glenelg WWTP C&D Plant Final Effluent A/C (ECOLI GRAB) on 13/07/2016 05:59:00 AM System: Glenelg WWTP Zone: Glenelg (WWTP) | Type 2 | 2016-07-14 12:07:00 | 1
2016-2017 | INC-0009751 | Victor Harbor (Boot) WWTP | Filtered water turbidity spiked to a maximum of 5.84 NTU at 4:08pm and remained above 0.5NTU for a period of 25 minutes (average turbidity for the period was 3.6 NTU, volume of treated effluent ~41kL, 24 hour average turbidity = 0.15 NTU). Filtered water turbidity turbidity spiked to a maximum of >5NTU at 8:42pm and remained above 0.5NTU for a period of 13 minutes (average turbidity for the period was 2.1 NTU, volume of treated effluent ~41kL, average 24 hour turbidity = 0.24 NTU) | Type 2 | 2016-07-01 14:16:00 | 1
2016-2017 | INC-0012777 | Mount Burr WWTP | Mount Burr Imhoff tank overflow at 9.45am on 29/10/16. Approx 25KL of water pumped to Imhoff over 50min from Mount Burr SPS1 - source of extra waste water unknown. Water volume too much to flow through imhoff and biofilter resulting in a minor overflow. | Type 3 | 2016-10-31 14:21:00 | 1
2016-2017 | INC-0019911 | Victor Harbor (Boot) WWTP | Due to ongoing issues with membrane tank 2 at Victor Harbor WWTP, the filtered water turbidity spiked over 0.5 NTU throughout several periods in the day. The turbidity spikes were initially attributed to the clean which was carried out on this membrane tank on 30/6 however it has since been discovered several plates have also failed. | Type 2 | 2016-07-05 13:34:00 | 1
2016-2017 | INC-0025805 | Heathfield WWTP | Power Outage related Type 2 WW incidents (regional WWTPs) - 12:15pm 29/9/16 - high turbidity if Heathfield WWTP effluent | Type 2 | 2016-09-29 14:03:00 | 1
2016-2017 | INC-0031970 | Glenelg Waste Water Treatment Plant | Switchboard feeding chlorine disinfection system failed at 5:13 meaning effluent discharged to sea was not being disinfected. Power was restored and disinfection reinstated at 7:32. Chlorine dose was increased to elevate residual in contact tank as quick as possible. Further work to identify and rectify root electrical problem is ongoing. Approximately 2.4 ML of undisinfected water was discharged DHA advised at 7:36. DHA advised to take shore line samples in line with outfalls and 100 and 200 m on either side and analyse for enterococci. Given that beach usage is low at this time of the year, no beach closure is required. EPA advised at 7:43. No action advised at this stage. | Type 1 | 2016-08-31 08:46:00 | 1
2016-2017 | INC-0033500 | Victor Harbor (Boot) WWTP | TRILITY Victor Harbor pump station 2 started up at 4:38am, reached a maximum CT of 28.1 mg.min/L before quickly falling away. Production was stopped at 5:24am at a CT 14.7mg.min/L. CT was <17 mg.min/L for a period of 6 mins. Discharge to the Inman River was occuring at the time, so no interruption to the reuse supply was experienced. | Type 2 | 2016-11-04 11:21:00 | 1
2016-2017 | INC-0033505 | Victor Harbor (Boot) WWTP | Victor Harbor WWTP high filtered water turbidity experienced over the 24 hour period which saw the turbidity >0.5 NTU for 3.3 hours (cummulative) on the 7/11/2016. Turbidity greater than 1 NTU for a period of 16 mins. Root cause suspected to be turbidity breakthrough from membrane tank 3. Tank has been isolated with a physical clean to commence on the 8/11/16 - membranes to be inspected with any failed plates removed and replaced. | Type 2 | 2016-11-07 15:59:00 | 1
2016-2017 | INC-0038261 | Glenelg Waste Water Treatment Plant | GAP production auto shut down due to low C.t. <16mg.min/L at 12:00pm Saturday 12 November. | Type 2 | 2016-11-12 12:00:00 | 1
2016-2017 | INC-0038272 | Victor Harbor WWTP | E.coli result 68MPN/100mL post CT tank (SP92139). Sample taken over 24 hours after the previous PS2 run (PS2 stopped at 3:23AM on the 13/11 and restarted at 10:48am on the 14/11 with the sample taken 14/11 ~8:00am). The water in this line is used for service water throughout the plant, meaning water does flow back through this line from the FWSL (an open lagoon) if PS2 hasn't run frequently enough to refill from the balancing storage. The CT was in spec in both pump runs either side of which the sample was taken, with the CT sitting around the 40-50mg.min/L mark. | Type 2 | 2016-11-15 10:45:00 | 1
2016-2017 | INC-0038313 | Glenelg Waste Water Treatment Plant | Loss of both Primary and secondary SAPN power supply resulted disinfection failure for >1 hour. | Type 1 | 2016-11-11 16:54:00 | 1
2016-2017 | INC-0038340 | Port Lincoln WWTP | As employee was reversing the Isuzu truck he clipped a bollard and dented it. | Type 3 | 2016-11-17 12:30:00 | 1
2016-2017 | INC-0038394 | Port Lincoln WWTP | Received an email Sunday morning about the strong odour at the PL WWTP. | Type 3 | 2016-11-27 08:30:00 | 1
2016-2017 | INC-0038436 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | High pH wastewater detected at Lobethal WWPS potential to impact the process at the Bird in Hand WWTP | Type 3 | 2016-12-04 05:00:00 | 1
2016-2017 | INC-0038490 | Christies Beach WWTP | Train 6 automatic maintenance clean performed a 5:00 am Saturday 10th, this caused some material to become logged in the turbidity meter. Train automatically started production at 11:47 and was shutdown after the PT was altered via a SCADA alarm at 12:34. | Type 2 | 2016-12-12 08:38:00 | 1
2016-2017 | INC-0038534 | Angaston WWTP |  | Type 1 | 2016-12-17 11:15:00 | 1
2016-2017 | INC-0038535 | Christies Beach WWTP | Upon arrival at site the Process Technician found potable water entering the site storm water system, this water made its way to the storm water collection lagoon before overflowing into Christies Creek. Potable supply is unmetered however it is estimated that >50KL was discharged into Christies Creek. | Type 2 | 2016-12-18 06:50:00 | 1
2016-2017 | INC-0038583 | Heathfield WWTP | Heathfield WWTP high effluent turbidity due to high incoming flow, power outage and PLC loss | Type 1 | 2016-12-28 03:30:00 | 1
2016-2017 | INC-0038634 | Port Augusta East WWTP | The storm event over the Christmas period at Port Augusta has resulted in the failure of the inlet and outlet flow meters at the Pt Augusta East WWTP. The failure is likely due to a lightning strike or electrical surge at the plant. | Type 3 | 2017-01-04 17:05:00 | 1
2016-2017 | INC-0038753 | Mannum WWTP |  | Type 1 | 2017-01-18 16:01:00 | 1
2016-2017 | INC-0038800 | Gumeracha WWTP | Forestry SA knocked the top off the air valve on the recycled water main leading to the Gumeracha forest adjacent to the river Torrens. resulting in approx 24 kL of treated recycled water entering the river. The river is flowing but quite slowly. | Type 2 | 2017-01-24 14:00:00 | 1
2016-2017 | INC-0038907 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | WAS sump flow to thickener stopped, this occurred while sludge thickener was running which for some reason didn't shut down, The liquid poly continued to be pumped to the thickener ,filling it up with the undiluted poly,for around 3 hrs,(SCADA GRAPH) stopped poly dosing by hitting E/stop this also stops/fault every unit in WAS system I then noticed WAS e/stop does not alarm to c/centre , it does bring up a General Fault though have Checked other E/stop alarms and they are the same I think this leaves a gap in safety as general faults can be triggered by minor faults and wont be escalated if the operator doesn't respond immediately to the c/center call | Type 3 | 2017-02-06 14:49:00 | 1
2016-2017 | INC-0038964 | Port Lincoln WWTP | The one of the two PLC units (duty/standby) running the operation of the IDEA basins at the Pt Lincoln WWTP failed. On investigation, it was identified that the version unit is no longer available and potentially required updating to the latest version. During testing to determine if the newer version is supported, the other PLC crashed resulting in loss of automatic control of the basin | Type 2 | 2017-02-08 11:35:00 | 1
2016-2017 | INC-0039050 | Port Augusta Prison WWTP | Sampling triggered by a change in lagoon colour has resulted in a microcystis flos-aquae count of 842,000 cells/mL | Type 1 | 2017-02-22 16:37:00 | 1
2016-2017 | INC-0039102 | Murray Bridge WWTP | Influent main from Pathways Estate clipped by push tube rig during investigation of soil contamination at the plant. Sewer flowed onto site into the reedy area west of the old sludge scrapes. All overflow was contained onsite and did not enter any watercourses or the river. | Type 3 | 2017-03-01 11:00:00 | 1
2016-2017 | INC-0039174 | Port Lincoln WWTP | > 10% of UV lamps fail and supply is not stopped. It was identified that 6 lamps (representing 10% of the UV lamps) had failed at approx. midday on 9/3. A review of the PLC alarm faults show the lamps failed at 16:13 on the 8/3 without shutting down the reuse system. | Type 1 | 2017-03-09 16:13:00 | 1
2016-2017 | INC-0039182 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2016-2017 | INC-0039365 | Gumeracha WWTP |  | Type 2 | 2017-04-07 14:45:00 | 1
2016-2017 | INC-0039402 | Murray Bridge WWTP | Odour complaint has been received from the public via EPA - Odours occurring overnight and in the morning when SE wind/breeze blowing. | Type 3 | 2017-04-11 16:28:00 | 1
2016-2017 | INC-0039467 | Port Augusta West WWTP | After dumping a load of sewer from Burgoyne SPS, contractors slipped off road on departure in very wet, slippery dark conditions. | Type 3 | 2017-04-24 22:00:00 | 1
2016-2017 | INC-0039507 | Whyalla WWTP | SA Water received three odour complaints within 24 hours, by residents located in Mullaquana and Whyalla Norrie. In undertaking visual and olfactory inspection of the WWTP and surrounding area, there has been no apparent odour detected. | Type 2 | 2017-05-02 18:00:00 | 1
2016-2017 | INC-0039521 | Christies Beach WWTP | AB plant PLC CPU failure resulted in the AB effluent disinfection system shutting down without SCADA notification or alarm to plant on call process technician. Operator became aware of issue during his morning plant inspections. Investigation indicates that disinfection system was in fault from 8PM Friday 5th through until 9:00am Saturday 6th with approx. 6ML of un-disinfected effluent discharged.. | Priority Type 1 | 2017-05-06 08:45:00 | 1
2016-2017 | INC-0039570 | Finger Point WWTP | The chlorine residual of disinfected waste water into the ocean was not monitored with an analyser for a number of hours due to sample water pump fault. A pump fault occurred at 3:42am, which is when the residual went to zero. The fault was rang through to workshop a few hours later and corrected, by a workshop person. | Type 3 | 2017-05-15 06:40:00 | 1
2016-2017 | INC-0039577 | Whyalla WWTP | Desludging Contractor at Whyalla WWTP stopped work when an electrical cable was found wrapped around their desludging dredge's auger. | Type 3 | 2017-05-16 06:30:00 | 1
2016-2017 | INC-0039579 | Heathfield WWTP |  | Type 2 | 2017-05-16 12:00:00 | 1
2016-2017 | INC-0039748 | Angaston WWTP | Milky looking substance detected at the inlet to the Angaston WWTP | Type 3 | 2017-06-07 13:45:00 | 1
2016-2017 | INC-0039792 | Finger Point WWTP | Finger Point WWTP, chlorine dosing station chlorine residual lost due to injection bores having an electrical fault. The chlorine residual was "0" on SCADA and the control desk rang the alarm through to our Workshop on call person. | Type 3 | 2017-06-18 11:01:00 | 1
2016-2017 | INC-0039827 | Angaston WWTP | High fluoride concentrations were detected by Trade Waste in Capral's routine weekly sampling sent to the AWQC. Capral are permitted to discharge up to 12mg/L of fluoride into the Angaston network however due to an issue at their plant they discharged effluent from the 1st to the 30th of May with F concentrations between 15 - 20mg/L. This discharge bypasses primary treatment and is sent straight into Lagoon 1. | Type 3 | 2017-06-15 14:52:00 | 1
2016-2017 | INC-0039862 | Finger Point WWTP | Weir 1 failed to raise after settling and mixed liquor was flowing over into polishing lagoons fro approx 1.45hr until operator was able to manually wind weir up | Type 3 | 2017-06-29 19:48:00 | 1
2016-2017 | INC-0039871 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Mt Barker council reported receiving correspondence from the owner of the Hahndorf Resort reporting odours attributed to the Hahndorf WWTP | Type 3 | 2017-05-16 13:00:00 | 1
2017-2018 | INC-0039884 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2017-2018 | INC-0039917 | Angaston WWTP | Inability to maintain chlorine residual to customer due to high chlorine demand of effluent | Type 3 | 2017-07-10 09:30:00 | 1
2017-2018 | INC-0040016 | Mount Burr WWTP | Tractor driven over stump, breaking battery box, step, hydraulic fitting and cabin door | Type 3 | 2017-07-26 11:10:00 | 1
2017-2018 | INC-0040073 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | A small quantity < 10kL of untreated wastewater was discharged to the Hahndorf WWTP stormwater system and then to the creek due to high inflow hence high level in ditch 1 | Type 2 | 2017-08-06 10:20:00 | 1
2017-2018 | INC-0040076 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Given the high rainfall the old lagoons at Bird in Hand have filled and lagoon 5 is now overflowing and discharging to the creek | Type 2 | 2017-08-07 09:41:00 | 1
2017-2018 | INC-0040203 | Port Lincoln WWTP | When the grit and screen tank at PL WWTP was emptied for it's 6 monthly clean, a significant amount of fat and grease build up was observed. | Type 3 | 2017-08-29 12:06:00 | 1
2017-2018 | INC-0040251 | Port Augusta West WWTP | During daily operational inspection, the operator noticed that the lagoon level at Port Augusta West WWTP was significantly higher than he has previously seen it. Upon further investigation it appears that one of the transfer valves has failed in a closed position and was preventing effluent from exiting the lagoon. | Type 3 | 2017-09-06 09:30:00 | 1
2017-2018 | INC-0040348 | Aldinga WWTP | Leak identified (visually) on Colville Rd, Aldinga from the Tinlins re-use main. This main supplies treated wastewater to the Tinlins vinyards for irrigation. The minor leak was discharging to the roadside natural culvert. Review of SCADA trends indicate that it is possible the leak has been ongoing since may have been occurring since 27/8/17, estimated total volume treated wastewater over 24 days is 830kL. | Type 2 | 2017-09-20 13:00:00 | 1
2017-2018 | INC-0040472 | Gumeracha WWTP | Discharge of treated, chlorinated (0.2mg/L Cl residual) from emergency soakage trench in the Forestry area north-west of the plant as irrigation from Joysons lagoon was not occurring. This discharge has then flowed into a local drainage line which discharges into the Torrens River | Type 1 | 2017-10-11 10:25:00 | 1
2017-2018 | INC-0040517 | Finger Point WWTP | Tail Light panel contacted bollard as truck was turning - Tail light panel bent and cracked. | Type 3 | 2017-10-19 13:00:00 | 1
2017-2018 | INC-0040520 | Whyalla WWTP | As I was trying to scoop up some tree debris into scraping bucket, the bucket caught onto the edge of the front bumper bar (stabilizer bar). As quick as it was to catch the bar it was to much strain on the weld and snapped clean off leaving the swing arm to be free to move towards and outwards of excavator cabin. | Type 3 | 2017-10-19 15:00:00 | 1
2017-2018 | INC-0040562 | Port Lincoln WWTP | High turbidity (>2NTU) plant shutdown alarm occurred at 0055, shutting down the raw water pumps feeding the reuse tank.. | Type 2 | 2017-10-26 00:55:00 | 1
2017-2018 | INC-0040563 | Port Lincoln WWTP | Plant shutdown due to high turbidity in the after filter product water, follow on from INC-0040562 | Type 2 | 2017-10-26 11:36:00 | 1
2017-2018 | INC-0040587 | Glenelg Waste Water Treatment Plant | Loss of treated effluent disinfection on C/D plant flume/outlet for >1hr due to system being offline to repair regulator. Works extended beyond 1hr (commencing 8:24am and system back online at 9:25am = 61mins). During this time there was no disinfection on C/D plant outlet however disinfection was retained on B Plant outlet (separate outfalls). The volume of undisinfected treated effluent discharged is estimated at approx. 0.7ML. | Type 1 | 2017-10-31 09:25:00 | 1
2017-2018 | INC-0040692 | Port Lincoln WWTP | The turbidity of the filtered reuse water was above 2NTU for 50 mins, the plant automatically shut down | Type 2 | 2017-11-15 08:30:00 | 1
2017-2018 | INC-0040697 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Leak approx. 10L on Sodium hydroxide system mixed with approx. 3000L of rain water in bund | Type 3 | 2017-11-16 08:55:00 | 1
2017-2018 | INC-0040769 | Victor Harbor (Boot) WWTP | The post-membrane filtered water exceeded 1.0 NTU from 17:41 to 19:06 (Avg. 2.2NTU) and again from 19:12 to 20:14 (Avg. 1.9 NTU). This water was stored in the balancing storage lagoon (BSL) on-site, with no water transferred through to reuse customers. UV disinfection remained compliant throughout the period with and 24hr average of UVT of 66%. No instantaneous UVT non-compliance was observed throughout the turbidity spikes. | Type 1 | 2017-11-26 18:41:00 | 1
2017-2018 | INC-0040784 | Angaston WWTP | Angaston WWTP: High chlorine demand (notification only) | Type 3 | 2017-11-28 12:00:00 | 1
2017-2018 | INC-0040915 | Heathfield WWTP | Pipe coming from the return process pump split over night causing an estimate discharge of 4kL to the environment, a small amount of this was sludge which I believe has been contained onsite with some water run off leaving the property boundary and heading towards our discharge point | Type 2 | 2017-12-12 08:00:00 | 1
2017-2018 | INC-0041050 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | Non-routine sampling of the polishing lagoon at Leigh Creek WWTP results showed a large concentration (39,600,000 cells/mL) of toxin producing BGA. We have no toxin results. | Type 3 | 2018-01-03 15:00:00 | 1
2017-2018 | INC-0041053 | Aldinga WWTP | SP41938 Aldinga WWTP - Final Effluent AC (to Lagoon 1) | Type 1 | 2018-01-04 10:30:00 | 1
2017-2018 | INC-0041068 | Whyalla WWTP | Owner of the Whyalla Caravan park called the customer call centre to report an odour coming from the Whyalla WWTP. This customer has complained 4-5 times in the last 6 months. Customer reported that odour improved since desludging works occurred in June/July of 2017 but she noticed a strong odour again on the 30/12/17. | Type 3 | 2017-12-30 09:16:00 | 1
2017-2018 | INC-0041174 | Whyalla WWTP | A customer odour complaint was called through to the CCC today, for Whyalla. It is believed the odour is coming from the lagoon WWTP. The WWTP has been under aerated recently due to a faulted aerator. Additionally the previous week has been above 40C every day. At this stage there is very little we can do, hopefully the wind starts to swing around and is blowing away from town. | Type 2 | 2018-01-22 14:35:00 | 1
2017-2018 | INC-0041189 | Whyalla WWTP | Odour complaint received from Owner of the Caravan Park on Mullaquana Road | Type 3 | 2018-01-23 08:38:00 | 1
2017-2018 | INC-0041193 | Whyalla WWTP | Odour complaint coming from WWTP | Type 3 | 2018-01-24 10:14:00 | 1
2017-2018 | INC-0041194 | Whyalla WWTP | Public odour complaint | Type 3 | 2018-01-24 10:44:00 | 1
2017-2018 | INC-0041242 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | High turbidity alarm was triggered at 1:12 am last night, suspected was caused by the cut in works being undertaken last night. Approximately 100 kl was transferred to ditch #1 by networks that may have short circuited through the clarifier | Type 3 | 2018-01-31 01:12:00 | 1
2017-2018 | INC-0041252 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | With the change in color of the plant inflow the UVT% dropped under the agreed lower limit (55%), lower limit reached was 52% | Type 3 | 2018-01-31 16:00:00 | 1
2017-2018 | INC-0041306 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | The UVT of the effluent dropped to 50% due to the increased color in the influent evident since the increased production at the Lobethal Abattoir | Type 3 | 2018-02-12 10:18:00 | 1
2017-2018 | INC-0041311 | Port Augusta Prison WWTP | Recent sampling from Port Augusta Prison WWTP has identified toxin producing microcystis flos-aquae at 17600 cells/mL at the outlet of the WWTP. | Type 2 | 2018-02-12 11:48:00 | 1
2017-2018 | INC-0041346 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | The influent to the plant contains a color that is difficult to treat and is therefore still present in effluent and causing the UVT to drop below 50 %. The effluent from the plant is low in turbidity and nutrient concentration. | Type 2 | 2018-02-15 09:08:00 | 1
2017-2018 | INC-0041381 | Port Augusta Prison WWTP | Fortnightly partial algal sampling is done at the WWTP to monitor the growth of blue green algae, recent sampling results from 05/02/2018 indicate a Microcystis flos-aquae cell count of 76,000 cells/mL. | Type 1 | 2018-02-20 15:19:00 | 1
2017-2018 | INC-0041397 | Christies Beach WWTP | Multiple plant alarms received 22/2/18 between 4:20am and 4:56am (water on floor, on-site re-use tank level low). Process technician attended site at approx. 5:20am and identified 6" aeration pipe feeding the pre-aeration tanks had failed, rupturing adjacent treated effluent line (or vice versa). Water has overflowed to the galleries causing partial flooding and to the on-site stormwater system and subsequently to Christies Creek. The estimated volume of treated chlorinated effluent discharged to the Christies Creek is 600kL. Potential to reach adjacent Christies Beach via Creek, however note the spill is treated and disinfected (chlorination / UV) effluent. Creek outlet checked and noted minor flow, however unable to establish if a result of spill or natural flows. | Type 2 | 2018-02-22 05:20:00 | 1
2017-2018 | INC-0041467 | Heathfield WWTP | Heathfield WWTP Centrifuge centrate return pipe work leaking at flange joint between pump and lagoon discharge, resulting in centrifuge centrate leaking down side embankment onto boundary fence. This pipe work is not the usual discharge path and is normally used to pump rainwater run off from the drying area sump. Volume of leak was small today and was contained on boundary of fence, as the centrifuge had only been running for under 1hr. Unknown if pipe was leaking previously or how long this pipework was in use. | Type 3 | 2018-03-03 09:00:00 | 1
2017-2018 | INC-0041657 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Fire extinguisher had dislodged from extinguisher bracket holder when opening canopy door extinguisher fell crushing handle and pin discharging contents | Type 3 | 2018-03-26 13:00:00 | 1
2017-2018 | INC-0041710 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | As above and photos sent to Rudi & Gretchen | Type 3 | 2018-04-04 10:00:00 | 1
2017-2018 | INC-0041767 | Heathfield WWTP | Pumped in lagoon No1 supernatant into the inlet works to lower level coming into winter. Pumping started in the morning and ran into the early evening before meter high alarm went off. Turbidity stayed high in high flows for 48 hours before Chlorine was switched off. No adverse affects to plant other than high turbidity levels. | Type 3 | 2018-04-05 11:00:00 | 1
2017-2018 | INC-0041802 | Murray Bridge WWTP | Reuse pump lifted from chamber lowered to flat ground (Soil) for inspection and replacement of lifting chain. Lifting hook disconnected to make room for new lifting assembly to be attached. Whilst in the process of disconnecting 2nd pump for lifting about 10 min after the previously lifted pump fell onto tank cover grate damaging 1 panel. Due to run off of water from the pump after a duration it had made the ground soft and unstable with the pump listing and falling to one side. No personnel within 3m of pump. | Type 3 | 2018-04-12 11:00:00 | 1
2017-2018 | INC-0041806 | Heathfield WWTP | Power failure to whole of plant(@08:30). Generator started once on site to return power to essential services and chlorine started (@09:30). High flows but plant coping ok. Had to switch off essential services to run blower as power from generator not sufficient to run both. Ran blower No. for 30 mins(@10:30) to keep Biomass happy. Switched back to essential services and monitored plant performance. Power back online @14:25. Multiple resets required to bring plant back online completely. Dewatering UPS had to be bypassed to provide power to board. | Type 3 | 2018-04-17 08:22:00 | 1
2017-2018 | INC-0041872 | Gumeracha WWTP | Sample tap at Gumeracha forest irrigation line to forest not locked and left in open position. - whilst doing a inspection of the forest irrigation I noticed the sample tap was left unlocked and open, with no method of locking the tap closed to prevent public use / tampering. - recommend installing a yellow lockable sample box over the top of the tap. | Type 3 | 2018-04-30 09:00:00 | 1
2017-2018 | INC-0041883 | Port Augusta West WWTP | The annual RPZ inspection has identified a fault in the second stage of the RPZ. | Type 3 | 2018-05-01 11:59:00 | 1
2017-2018 | INC-0041963 | Port Augusta West WWTP | The PAW WWTP chlorination system is consistently going into low vacuum - after a period of 50 minutes this shuts down the chlorination system and stops supply to the PA Golf Club. I have had several complaints from the golf club over the inconsistent supply of water. We are currently unsure what the cause of the low vacuum is. | Type 3 | 2018-04-26 12:00:00 | 1
2017-2018 | INC-0042351 | Finger Point WWTP | Power outage 5.52-12.30pm. Interruption to aeration process affecting treatment process | Type 3 | 2018-05-29 05:52:00 | 1
2017-2018 | INC-0042352 | Finger Point WWTP | Power Outage 18.40 - 22.05 - interrupting aeration process | Type 3 | 2018-06-14 18:40:00 | 1
2017-2018 | INC-0042353 | Finger Point WWTP | Power Outage disrupting aeration process | Type 3 | 2018-06-17 02:30:00 | 1
2017-2018 | INC-0042708 | Finger Point WWTP | Power Outage 2.14 - 3.10 = 0.56hrs Loss of aeration process | Type 3 | 2018-03-19 02:14:00 | 1
2017-2018 | INC-0042709 | Finger Point WWTP | Power Outage 12.05 - 13.57 = 1.52hrs Aeration Process Interruption | Type 3 | 2018-01-12 12:05:00 | 1
2017-2018 | INC-0042710 | Finger Point WWTP | Power Outage 22.53 - 1.21 = 2.28 hrs Aeration process interruption | Type 3 | 2017-10-28 22:53:00 | 1
2018-2019 | INC-0042399 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | main entry to plant blocked by parked cars ,networks /tankers would not have been able to gain entry to lagoon dump area | Type 3 | 2018-07-08 09:00:00 | 1
2018-2019 | INC-0042703 | Finger Point WWTP | Power Outage 16.48 - 12.30 = 9.5hrs Also loss of comms from 7pm - 7.38am. Aeration not operating = process negatively affected, operators and ops control could not monitor site externally. | Type 3 | 2018-07-26 16:48:00 | 1
2018-2019 | INC-0042772 | Heathfield WWTP | Heathfield WWTP: UV system over capacity | Type 3 | 2018-08-03 08:00:00 | 1
2018-2019 | INC-0042774 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird-In-Hand WWTP: UV System Low UV Dose Hi Priority Alarm | Type 3 | 2018-08-03 07:30:00 | 1
2018-2019 | INC-0042789 | Heathfield WWTP | High turbidity on effluent discharge to the creek due to high flow caused by heavy rainfall. Turbidity increased and peaked at 40 NTU, less than discharge creek turbidity, before coming back under control using plant operational changes. Chlorine disinfection initiated due to high flow event and residual maintained during high turbidity discharge. | Type 2 | 2018-08-06 10:00:00 | 1
2018-2019 | INC-0042804 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | There is a strong odour coming from the Port Pirie WWTP. Most likely due to desludging occurring onsite. Notified by the plant operator, who can smell odour onsite and on the outskirts of town (depending on wind direction). | Type 3 | 2018-08-07 11:06:00 | 1
2018-2019 | INC-0042808 | Mount Burr WWTP | Fouled screen and removal of Hi Level sensor caused level in tank to almost overtop sides | Type 3 | 2018-08-08 14:32:00 | 1
2018-2019 | INC-0042809 | Mount Burr WWTP | Mount Burr WWTP: Biofilter arms not rotating During concrete remediation works, the Biofilter arms were not rotating as the Recirculation Pumps were not in operation, this may have caused damaged to the Biofilm on the media | Type 3 | 2018-08-08 14:36:00 | 1
2018-2019 | INC-0042865 | Millicent WWTP |  | Type 3 | 2018-08-15 17:30:00 | 1
2018-2019 | INC-0042914 | Finger Point WWTP | Finger Point WWTP: Chlorine dosing system, Auto Shutdown activated (unknown reason) Duration 50 minutes | Type 3 | 2018-08-23 14:30:00 | 1
2018-2019 | INC-0042934 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird-In-Hand WWTP: (Detergent/Loading) Foam incident | Type 3 | 2018-08-28 15:05:00 | 1
2018-2019 | INC-0043017 | Heathfield WWTP | Heathfield WWTP site generator to small to run whole of site. When AC power supply is interrupted compromised process is experienced. When AC power was reinstated A recycles pumps, DAFT system, Blower #4 and centrifuge would not remotely reset. | Type 3 | 2018-09-11 13:00:00 | 1
2018-2019 | INC-0043027 | Heathfield WWTP | VFD to Blower #4 does not control Blower. The blower its self runs @ 100% only. | Type 3 | 2018-09-12 13:00:00 | 1
2018-2019 | INC-0043047 | Angaston WWTP | Angaston WWTP: Lagoon #1 Low alkalinity, low pH, high nitrate, Turtle deaths | Type 3 | 2018-09-07 07:30:00 | 1
2018-2019 | INC-0043129 | Heathfield WWTP | on routine inspection of Heathfield WWTP noticed a dead magpie floating in clarifier tank number 2. | Type 3 | 2018-09-26 12:13:00 | 1
2018-2019 | INC-0043232 | Naracoorte WWTP (Treatment Works Rd) | Over the last 2 to 3 years Mt Gambier Electrical workshop has been called to the site to investigate why the PLC is not working. The PLC is an older Idec FC3 Open-net controller type, and has been suffering from I/O cards failures (3 to 4), which have been hard to identify. As you pull apart to Card rack and put it back together and everything will work fork a week or for several months till the next issue. Will be placing an OIR for this issue. While in this fault condition the plant will operate No 1 Pump off a High Level float, this was implemented approx. 18mths to 2 years ago as mitigation. | Type 3 | 2018-10-04 10:17:00 | 1
2018-2019 | INC-0043235 | Millicent WWTP | E.coli result was 2400 MPN/100mL. There was no irrigation at the time of detection. | Type 3 | 2018-09-06 10:00:00 | 1
2018-2019 | INC-0043236 | Millicent WWTP | E.coli result was 1300 MPN/100mL. There was no irrigation at the time of detection. | Type 3 | 2018-10-02 20:35:00 | 1
2018-2019 | INC-0043329 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | After a power flick at the Bird in hand Wastewater treatment plant resulting in lost coms from the dissolved oxygen probe and pH probe to SCADA, we had no air going to reactor A for approximately 4 hours, The resulting problem was a splitter fault causing an over current, | Type 3 | 2018-10-24 06:20:00 | 1
2018-2019 | INC-0043330 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | When Bio-gas mixing of the digester is occurring I noticed a leak coming from the flexible braided line leading to the gas mixing lances, | Type 3 | 2018-10-22 07:30:00 | 1
2018-2019 | INC-0043426 | Christies Beach WWTP | Unauthorised entry to CBWWTP overnight - vandals have opened sludge valve on strainpress at dewater plant in addition to multiple process water lines. Overflow of sludge and process water to onsite swale, to adjacent Christies Creek and to beach. Time & method of entry unknown, no SCADA or security alarms triggered. CCTV footage of offender at site is available on request from Andy Hendry. | Priority Type 1 | 2018-11-12 07:20:00 | 1
2018-2019 | INC-0043480 | Mannum WWTP | Whilst using the small excavator at Mannum WWTP to clear debris for new pad to erect tool shed at a later date, a branch pushed on hydraulic hose fitting which in turn the fitting started to leak hydraulic oil. | Type 3 | 2018-11-15 11:00:00 | 1
2018-2019 | INC-0043500 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2018-2019 | INC-0043641 | Heathfield WWTP | Low UV transmissivity (false) alarm Analyser full of air and solids | Type 3 | 2018-12-11 13:00:00 | 1
2018-2019 | INC-0043656 | Murray Bridge WWTP | Murray Bridge WWTP: Noise complaint from neighbor, solids extraction from Imhoff Tanks at the time | Type 3 | 2018-12-13 06:45:00 | 1
2018-2019 | INC-0043756 | Port Lincoln WWTP | During daily inspections the operator noticed puddles around the inlet splitter box at the Port Lincoln WWTP. As all other areas of the ground were dry and there had not recently been a rain she was able to determine that the splitter box had recently overflowed. The new rising main enables wastewater to be fed to the WWTP at a higher flow rate than previously occurred, causing the splitter box to overflow. The level sensor in the splitter box shows the level significantly increased prior to the puddles being observed, however, there is no high level switch within the splitter box that gives data on when the splitter box is overflowing (the level sensor's maximum level is lower than the overflow point). The new main's flow meter is currently not connected to SCADA so it is impossible to determine what flows the inlet works were receiving or even the exact time that the splitter box overflowed. | Type 2 | 2018-12-30 10:30:00 | 1
2018-2019 | INC-0043859 | Whyalla WWTP | hose clamp on pump had come undone causing wastewater to spray on to road and lagoon edge | Type 3 | 2019-01-17 08:30:00 | 1
2018-2019 | INC-0043940 | Whyalla WWTP | Five odour complaints have been received from Whyalla residents (Caravan Park and township). Lagoons 5 and 6 at the WWTP have become odourous. Additional aeration (four aerators instead of typically three) has been running since November 2018. Probable cause is hot weather leading to increased evaporation, resulting in reduced flow to and increased evaporation of Lagoons 5 and 6. | Type 2 | 2019-01-30 09:30:00 | 1
2018-2019 | INC-0043968 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Release of A/UV Effluent to Creek due to unplanned opening of Storage Bypass valve | Type 3 | 2019-01-31 15:45:00 | 1
2018-2019 | INC-0043976 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Release of A/UV Effluent to Creek due to unplanned opening of Storage Bypass valve | Type 2 | 2019-01-31 15:45:00 | 1
2018-2019 | INC-0043985 | Port Lincoln WWTP | On Sunday a high decant flow alarm was triggered, showing that one of the basins was decanting water although the decanting weirs were still up. Upon site inspection it was determined that the basin was overflowing as it had entered "storm mode" and not switched basins. Approximately 250kL overflowed from the basin into the polishing lagoon. Overflow is believed to be mostly settled effluent with low nutrients, further testing to occur today to confirm. AWQC samples will be taken today (routine samples) so anything out of the ordinary will be detected. Futher investigation suggests that multiple power flickers and a potential programming glitch could be the cause of the alarm. Currently everything is running smoothly. | Type 3 | 2019-02-03 13:15:00 | 1
2018-2019 | INC-0043995 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Temporary hose connection to new poly dosing system blew off around 8pm on 03/02/19 causing a high high level in the dosing bund, everything was contained onsite in the bund. | Type 3 | 2019-02-04 07:30:00 | 1
2018-2019 | INC-0044255 | Whyalla WWTP |  | Type 2 | 2019-03-04 14:50:00 | 1
2018-2019 | INC-0044265 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Found water straying out a short pipe after the meter on our neighbours property. Flooding down along his paddock had already started but it looked to have only been running for a short amount of time (1-2 hours guess), I isolated the outlet valve. | Type 3 | 2019-03-05 11:48:00 | 1
2018-2019 | INC-0044471 | Millicent WWTP | E.coli 1100 MPN/100mL | Type 3 | 2019-03-19 12:30:00 | 1
2018-2019 | INC-0044481 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2018-2019 | INC-0044509 | Port Augusta East WWTP | Aerator #3 at Port Augusta East WWTP went out on fault on Saturday 30/3. The fault alarm was activated, however, after two hours the alarm state went back to "normal". The OCC did not create a WO or phone anyone to have a look. The aerator remained off all day Saturday and Sunday. On Monday 1/4 electricians were unavailable to attend site and phoned the operator, unfortunately the issue could not be resolved and aerator remained off for all of Monday. | Type 3 | 2019-04-01 12:00:00 | 1
2018-2019 | INC-0044510 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2018-2019 | INC-0044533 | Victor Harbor (Boot) WWTP | E.coli 180 MPN/100mL is detected at the sampling location TRILITY Victor Harbor WWTP Treated Wastewater - Post Chlorine CT. After reviewing the Plant performance trends, it can be seen that Pump Station 2 (PS2) had not run since 8:40pm on 01/04/2019 and this sample was taken at about 8am on 02/04/2019. The PS2 run which finished at 8:40pm on 01/04/2019 was compliant with CT around 60mg.min/L. Hence the sample taken at about 8am on 02/04/2019 is not representative of chlorinated water produced by the Plant. Downgraded on 8 April 2019 by DHA and by SAW (Lisa Hannant). Repeat sample result confirms that the earlier sample is not representative. | Type 2 | 2019-04-03 11:14:00 | 1
2018-2019 | INC-0044587 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird in hand WWTP Scum trough leaking out of ground from clarifier wall, opened valve to scum trough and leak has stopped. crews to dig up and investigate | Type 3 | 2019-04-09 14:00:00 | 1
2018-2019 | INC-0044601 | Murray Bridge WWTP | As above | Type 3 | 2019-04-10 05:30:00 | 1
2018-2019 | INC-0044651 | Millicent WWTP | Location 46081: Irrigation Season Sampling - Outlet of sand filters E.coli 1600 MPN/100mL (Type 3) | Type 3 | 2019-04-08 12:40:00 | 1
2018-2019 | INC-0044700 | Port Pirie Activated Sludge WWTP (Kitchener Tce) |  | Type 3 | 2019-04-25 06:00:00 | 1
2018-2019 | INC-0044739 | Port Augusta West WWTP | The reuse main owned by the Port Augusta Golf club has burst inside the WWTP boundary. Estimated that 500 kL spilled from pipe onto SAW site and then out of site, across road and down onto other side of road. | Type 2 | 2019-05-02 10:00:00 | 1
2018-2019 | INC-0044949 | Murray Bridge WWTP | Murray Bridge Effluent Reuse Wetland Outlet Pond B E.coli 4000 orgs/100mL | Type 2 | 2019-05-23 10:00:00 | 1
2018-2019 | INC-0045024 | Angaston WWTP | After collecting samples, reversing back close to a bollard. Drive over an unseen star picket next to the bollard. This somehow jumped up and jammed into the sump on the bottom of the engine. Shutdown engine immediately and organised tow. | Type 3 | 2019-06-11 07:00:00 | 1
2018-2019 | INC-0045081 | Mannum WWTP | Whilst chaining the Mannum WWTP Imhoff tank 1, the rope suddenly frayed and snapped causing 2m of heavy chain to drop to the bottom of the Imhoff tank, LHS of the walkway near the inlet chamber structure. Chain and 3m of attached rope dropped to bottom of tank ( approx. 8m deep) -Potential for chain for foul wasting outlet pipe ( blockage) -Potential for chain to move in tanks get caught in valve when wasting preventing operation of valve. | Type 3 | 2019-06-14 14:00:00 | 1
2019-2020 | INC-0045595 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Storm in area ... high hydraulic load and turbidity inflow | Type 3 | 2019-08-08 17:30:00 | 1
2019-2020 | INC-0045597 | Heathfield WWTP | High hydraulic load ... high turbidity inflow | Type 3 | 2019-08-08 17:30:00 | 1
2019-2020 | INC-0045623 | Finger Point WWTP | Storm damage to SAPN infrastructure resulted in 19hr power outage to Finger Point WWTP - no aeration process. Interruption to treatment process. Operators travelling to plant at night to refuel generator and re-start plant in poor weather conditions. | Type 3 | 2019-08-08 23:15:00 | 1
2019-2020 | INC-0045650 | Murray Bridge WWTP | Murray Bridge Lagoon WWTP (Govt Rd) Lagoon #1 Aerator #5: Aerator Fault: Initially thought to be Motor/Gearbox ... turned out to be moisture in electrical connection | Type 3 | 2019-08-14 12:00:00 | 1
2019-2020 | INC-0045774 | Normanville WWTP | Normanville WWTP A/C Effluent: E.coli 730 MPN/100mL (Free chlorine 1.9 mg/L, Total chlorine 2.9 mg/L) | Type 2 | 2019-08-26 13:20:00 | 1
2019-2020 | INC-0045860 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | tree outside Hahndorf WWTP had fallen over & was laying on top of fence. the tree had pushed the wire of the fence down & was protruding into the contractors Septic Trial work area. | Type 3 | 2019-09-13 11:37:00 | 1
2019-2020 | INC-0045885 | Myponga Beach WWTP | whilst travelling from Woodside to Normanville WWTP in small tipper truck with load of 10mm screenings for work at Normanville WWTP. I pulled over to let vehicles pass in a parking bay between Meadows & Myponga, where a vehicle pulled up beside me & got out then informed me that whilst she was travelling behind me, a small rock flicked up & chipped her windscreen. | Type 3 | 2019-09-17 08:20:00 | 1
2019-2020 | INC-0045936 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | E.coli 160 MPN/100mL Free chlorine 0.4 mg/L Total chlorine 1.6 mg/L | Type 3 | 2019-09-20 05:59:00 | 1
2019-2020 | INC-0045945 | Wirrina Cove WWTP | weeping observed from lagoon 2 wall to local stormwater side entry pit | Type 2 | 2019-09-25 12:00:00 | 1
2019-2020 | INC-0046088 | Mount Burr WWTP |  | Type 3 | 2019-10-12 20:05:00 | 1
2019-2020 | INC-0046277 | Finger Point WWTP | During a crane lift, my finger slipped off the trigger of the hand piece whilst lifting the boom up - causing the boom to jerk slightly and swing the crane hook into the truck cabin, causing minor damage. There was no load on the hook at the time. | Type 3 | 2019-11-01 13:00:00 | 1
2019-2020 | INC-0046312 | Normanville WWTP | Operator attended site after numerous alarms to detect lack of chlorine residual, with Plant in continual backwash for no reason. Unable to inhibit backwashing even with Backwash pumps inhibited. Unsure if chlorine had stopped dosing or not due to no trending available | Type 1 | 2019-11-04 12:00:00 | 1
2019-2020 | INC-0046323 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2019-2020 | INC-0046579 | Port Lincoln WWTP | The Port Lincoln Reuse plant ran out of Chlorine early hours this morning. This caused the Booster pump to fault however, as programmed, the reuse plant continued to run for 50mins and then shut down on low chlorine fault (chlorine level Discrepancy alarm). The supply was still available for the council until the tank was drawn down to bottom water level. UV disinfection was still operating. Council were notified that they have no water this morning and I am waiting for a call back so I can explain the reasons. | Type 3 | 2019-11-18 07:30:00 | 1
2019-2020 | INC-0046607 | Mount Burr WWTP |  | Type 3 | 2019-11-17 11:50:00 | 1
2019-2020 | INC-0046609 | Millicent WWTP | Millicent Lagoon WWTP (Lossie Rd): Irrigation Effluent Location 46081 18/11/19: E.coli 2400 MPN/100 mL | Type 3 | 2019-11-18 09:40:00 | 1
2019-2020 | INC-0046633 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Ixom / Kalari delivered 25T of Alum sulphate solution to Bird In Hand WWTP on 21/11/2019, after the driver had finished discharging alum solution and had packed up his truck and hoses a trail of liquid up the driveway was noticed behind the truck leaving, this is usually water from when the connection hoses are are cleaned out. When I arrived on site today the trail of liquid has dried in to crystallised alum sulphate ( very hard underfoot away). I estimate a spill of 25 to 30 litres of solution has been spilled up 150 meters of road way. | Type 3 | 2019-11-22 11:00:00 | 1
2019-2020 | INC-0046727 | Heathfield WWTP | Heathfield WWTP Effluent After UV SP42969: Total; P 1.03 mg/L (greater than aspirations P&T Support limit of 1.0 mg/L) | Type 3 | 2019-11-21 08:00:00 | 1
2019-2020 | INC-0046734 | Normanville WWTP | Sludge overflow supernatant sump some stage during the night approximately 1kl | Type 3 | 2019-12-05 09:00:00 | 1
2019-2020 | INC-0046738 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd) A/C Effluent Location 4555 Suspended Solids 23 mg/L (greater than P&T aspirational limit of 10 mg/L) | Type 3 | 2019-11-08 08:00:00 | 1
2019-2020 | INC-0046743 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorination system: A combination of low flows, chlorine system changeover failure and PLC PID problems resulted in a lower than designated chlorine dose | Type 3 | 2019-12-06 10:22:00 | 1
2019-2020 | INC-0046758 | Mannum WWTP | The outlet of the Imhoff tanks at Mannum is severly restricted leading to the tanks backing up. | Type 3 | 2019-12-06 12:00:00 | 1
2019-2020 | INC-0046764 | Normanville WWTP | Normanville WWTP, Supernatant overflow, approximately 5 to 10kl of supernatant sludge overflowed to the swale inside treatment plant boundary over the weekend. | Type 3 | 2019-12-09 10:34:00 | 1
2019-2020 | INC-0046873 | Whyalla WWTP | Tripped aerator was reset to bring back online. This aerator pulled in the floating cable form another aerator, damaging the aerator, positioning ropes and unable to restart. | Type 3 | 2019-12-19 10:33:00 | 1
2019-2020 | INC-0046901 | Finger Point WWTP | The high pressure wash water line for screen screw press came loose, spraying water over screen area and filling bund. Bund pump stopped working as rag had been caught in the pump, causing a high level alarm and operator to be called. | Type 3 | 2019-12-21 08:30:00 | 1
2019-2020 | INC-0046919 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | BIH discharges had ceased at the beginning of summer with supply to recycled water customers. When the power faulted/changed over to the generator the valve to re-use storage closes automatically diverting flow to the weir and creek discharge. This did not generate an alarm as should have occurred. | Type 3 | 2019-12-23 12:19:00 | 1
2019-2020 | INC-0046990 | Gumeracha WWTP | Gumeracha Lagoon WWTP (Torrens Valley Rd): Location 454501 Chlorine Contact Pipe 24/12/2019 E.coli >2400 orgs/100mL | Type 3 | 2019-12-30 10:06:00 | 1
2019-2020 | INC-0046999 | Normanville WWTP | Decant pumps have stopped working potentially due to blockage. The decant effluent has flown into the overflow tank as it is meant to do, this tank has then overflowed into the creek. Due to Catastrophic conditions yesterday no operator was allowed onsite and the communication link to the plant failed therefore the overflow was only discovered this morning. | Type 1 | 2019-12-31 10:40:00 | 1
2019-2020 | INC-0047017 | Wirrina Cove WWTP | Wirrina WWTP, Decant tank, overflow at some stage over Christmas period. Effluent contained onsite | Type 3 | 2019-12-31 09:00:00 | 1
2019-2020 | INC-0047070 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | UV Disinfection Unit B 3 globes faulted causing the UV to Lagoon Valve to close. | Type 3 | 2020-01-09 06:30:00 | 1
2019-2020 | INC-0047071 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | On routine check/walk around plant, noticed a piece of Rotor Disk wedged up against the centre wall in Ditch 1. | Type 3 | 2020-01-09 08:00:00 | 1
2019-2020 | INC-0047116 | Bird In Hand WWTP | Noticed smoke form two patches of grass/weeds that had been burnt through from the fire event. On further inspection noticed a burning smell & felt that the two areas were warmer than usual. | Type 3 | 2020-01-15 10:00:00 | 1
2019-2020 | INC-0047127 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): UV Bypass Valve and UV sampling Pump Intermittent Failures | Type 3 | 2020-01-16 10:00:00 | 1
2019-2020 | INC-0047149 | Victor Harbor (Boot) WWTP | Daily average of UV transmission <60%, dropping below 60% from 8:30pm 17/1, as low as 56.8% 14:06pm 18/1. Operators onsite on 18/1 to assess caustic and coagulation dosing due to varying pH performance. UVT has been improving since and as of 19:30 19/1 is almost back to 60%. | Type 2 | 2020-01-18 12:00:00 | 1
2019-2020 | INC-0047173 | Port Lincoln WWTP | odour generated by dumping of Praziquantel by fishing industry into wastewater network. the odour is pungent and has on occasion caused nausea and headaches | Type 3 | 2020-01-15 11:28:00 | 1
2019-2020 | INC-0047174 | Port Lincoln WWTP | odour generated by dumping of Praziquantel by fishing industry into wastewater network. the odour is pungent and has on occasion caused nausea and headaches | Type 3 | 2020-01-14 11:29:00 | 1
2019-2020 | INC-0047175 | Port Lincoln WWTP | odour generated by dumping of Praziquantel by fishing industry into wastewater network. the odour is pungent and has on occasion caused nausea and headaches | Type 3 | 2020-01-09 11:32:00 | 1
2019-2020 | INC-0047176 | Port Lincoln WWTP | odour generated by dumping of Praziquantel by fishing industry into wastewater network. the odour is pungent and has on occasion caused nausea and headaches | Type 3 | 2020-01-03 11:34:00 | 1
2019-2020 | INC-0047182 | Murray Bridge WWTP | Murray bridge WWTP Imoff tank 4, Sludge overflow from Gas vent approx 1 kl of sludge overflowed | Type 3 | 2020-01-13 09:00:00 | 1
2019-2020 | INC-0047206 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Discharge to Creek approx 500 kL | Type 1 | 2020-01-27 11:00:00 | 1
2019-2020 | INC-0047207 | Port Lincoln WWTP | praziquantel odour detected onsite. | Type 3 | 2020-01-28 09:24:00 | 1
2019-2020 | INC-0047209 | Finger Point WWTP |  | Type 3 | 2020-01-25 14:00:00 | 1
2019-2020 | INC-0047250 | Port Lincoln WWTP | high rain flow event and power flicks caused overflow of splitter box and overloading of aeration basins. Causing washout of solids and process disruptions. | Type 3 | 2020-01-31 16:11:00 | 1
2019-2020 | INC-0047267 | Port Lincoln WWTP | Praziquantel used by the fishing industry discharge received at the treatment plant causing pungent odour | Type 3 | 2020-02-03 13:16:00 | 1
2019-2020 | INC-0047324 | Port Lincoln WWTP | Praziquantel discharge into sewage system by fishing industry detectable at the waste water treatment plant | Type 3 | 2020-02-06 12:33:00 | 1
2019-2020 | INC-0047377 | Port Augusta West WWTP | contractor was locked in toilet | Type 3 | 2020-02-11 13:21:00 | 1
2019-2020 | INC-0047382 | Murray Bridge WWTP | Murray Bridge Lagoon WWTP (Govt Rd): Effluent Reuse Wetland Outlet Pond B Location 4759: E.coli 6400 MPN/100mL | Type 2 | 2020-02-07 05:59:00 | 1
2019-2020 | INC-0047387 | Whyalla WWTP | Two complaints received through the media team on Facebook regarding odour issues in different areas around Whyalla. | Type 2 | 2020-02-12 14:00:00 | 1
2019-2020 | INC-0047441 | Finger Point WWTP |  | Type 3 | 2020-02-18 11:30:00 | 1
2019-2020 | INC-0047549 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | High than normal ammonia residual in Final Plant Effluent | Type 3 | 2020-02-28 14:38:00 | 1
2019-2020 | INC-0047585 | Finger Point WWTP | Finger Point WWTP Aerator 4 has broken a cable and come loose from its mooring. The electrical cable tray has been damaged. | Type 3 | 2020-03-03 09:33:00 | 1
2019-2020 | INC-0047726 | Victor Harbor (Boot) WWTP | Failure of the vacuum switch within the chlorine dosing system which cause failure of the chlorinator upon start up of the system. This resulted in 50mins of no chlorine residual between 9:53am and 10:43am at which stage the system was shut down as the issue could not be rectified remotely. Plant Operator then attended site to trouble shoot, at which time the failed vacuum switch was found. UV disinfection system is working. | Type 2 | 2020-03-16 09:04:00 | 1
2019-2020 | INC-0047763 | Port Lincoln WWTP | Wasting valve for Basin 1 failed in the open position causing 3days worth of wastings in 3 hours. Loss of solids to sludge lagoons | Type 3 | 2020-03-16 14:01:00 | 1
2019-2020 | INC-0047789 | Finger Point WWTP |  | Type 3 | 2020-03-11 14:35:00 | 1
2019-2020 | INC-0047923 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf WWTP: Location 4555 A/C Effluent E.coli 210 MPN/100mL | Type 3 | 2020-03-25 06:00:00 | 1
2019-2020 | INC-0048007 | Heathfield WWTP | Power outage at Heathfield WWTP this morning 04:19hrs, no notification of outage or of UV bypass failure UV bypass opened and failed open resulting in approximately 300kL of non-disinfected effluent to flow into contact tank and then creek until 11:00hrs UV system was still running and was very hot with no flow passing through. The UV sample pump had also run dry | Type 1 | 2020-04-11 11:00:00 | 1
2019-2020 | INC-0048043 | Port Lincoln WWTP | Reoccurring weir encoder faults causing basin faults/ process disruption . suspected cabling issues unable to repair/access due OHS issues around grid mesh removal. awaiting capital projects. this happens . weir faults are happening very often and plenty of unnecessary call outs and overtime. | Type 3 | 2020-04-17 08:46:00 | 1
2019-2020 | INC-0048123 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2019-2020 | INC-0048155 | Mannum WWTP | Mannum Lagoon WWTP (River Lane): Effluent reuse system: Presence of algae in Lagoon has increased the chlorine demand | Type 3 | 2020-04-30 09:17:00 | 1
2019-2020 | INC-0048225 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | rats have eaten through various cables ,with one of them being the main feed to the office. | Type 3 | 2020-05-08 12:57:00 | 1
2019-2020 | INC-0048246 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | • NGE contractor Perry’s Fuel Distributers attended site to re-fuel NGE’s 1200L fuel trailer. • The delivery driver connected his fuel nozzle to interstitial dip valve instead of fill valve. • As a result, the diesel sprayed out causing a spill. NGE Site Manager (SM) called for the operator to stop immediately • NGE Site Manager and Enerven SQE Advisor grabbed nearby spill kit and began clean up • The operator then connected to the other dip valve and the same thing occurred – NGE SM called for the operator to stop once again. The result being a loss of approximately 20-30L. | Type 3 | 2020-05-12 08:00:00 | 1
2019-2020 | INC-0048263 | Heathfield WWTP | At 14:45 noticed a VEOLIA Liquid Waste truck using the Septic Receival bay at Heathfield WWTP. At 15:45 noticed the VEOLIA Liquid Waste truck pulling out of bay & I thought to myself "he took longer than usual". A different company truck pulled in straight after to use the facilities & I noticed that he was having a problem with the hose for discharging. I walked up to see what the issue was & noticed that the hose & the pipework/valves for receiving were blocked up with sand. The VEOLIA truck was parked 20 meters up from the plant on the side of the road. I decided to speak to the driver about the issue that has been caused. Upon arriving on the drivers side of the VEOLIA truck, saw that the driver was on the phone so I patiently waited for him to finish his conversation & wind the window down. We pleasantly introduced ourselves & then I asked a few blunt & straight forward questions regarding to what he is/was transporting/delivering to the Wastewater Treatment Plant. His response was that he is cleaning out Septic Tanks in the township of Yankalilla & he has to bring the septic here. I replied by informing him of the issue that has just been caused by his delivery, & this treatment plant does not accept sand as it causes issues with the process & that this plant is not designed for such product. Informed this driver that no sand is to be delivered to this plant. Walked to receival station & gave a quick clean ready for next days work. | Type 3 | 2020-05-13 15:50:00 | 1
2019-2020 | INC-0048264 | Normanville WWTP |  | Type 3 | 2020-05-11 09:30:00 | 1
2019-2020 | INC-0048631 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Contractor Septic King who transfers Sludge from Hahndorf WWTP to Heathfield WWTP on a daily basis arrived onsite to Hahndorf WWTP & found that he has no access to fulfil his job as the entry gate to the treatment plant have had the Operator padlocks locked out of the link. Apparently this is the third time this has occurred & there is no room for a vehicle let alone a truck to turn around. As Operators we need access at all times. | Type 3 | 2020-06-19 08:40:00 | 1
2020-2021 | INC-0048878 | Normanville WWTP | Normanville WWTP: Normanville WWTP: Backwash Tank (Oveflow to Creek) Unknown issue at this stage has caused the Normanville WWTP Backwash Tank to overflow … repairs etc being instigated at time of reporting | Type 2 | 2020-07-14 13:00:00 | 1
2020-2021 | INC-0049271 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Hydraulic overload Due to high rainfall into area, higher than baseline inflows has caused a hydraulic overload through Clarifier #1 | Type 3 | 2020-08-19 08:30:00 | 1
2020-2021 | INC-0049289 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Contractor returning a solids bin after emptying whilst placing bin back onto weight bridge, bin struck metal conduct containing cable for solids conveyer & damaged cable. | Type 3 | 2020-08-20 11:30:00 | 1
2020-2021 | INC-0049291 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Due to high rainfall into area, higher than baseline inflows has caused a hydraulic overload through Clarifier #1. Disinfection functioning. | Type 2 | 2020-08-20 17:00:00 | 1
2020-2021 | INC-0049345 | Bolivar High Salinity Waste Water Treatment Plant | Severe leak formed on RAS4 pipework during hydro excavation, location suspected on joint between ASR4 wall and RAS pipe. ASR4 isolated/being pumped down to stop leak and allow for inspection/repairs. PEPS overflow into stabilisation lagoons whilst isolating ASR4 inlet from 9am to 9:25am | Type 2 | 2020-08-26 09:30:00 | 1
2020-2021 | INC-0049376 | Bolivar High Salinity Waste Water Treatment Plant | Subcontractor was engaged to expose the RAS pipe as it enters ASR tank # 4. During the Non destructive hydro-excavation process the work crew noticed an ingress of process fluid begin to appear in the excavation.This ingress of fluid began before the workers had located the pipe. Excavation permit was in place and work area was delineated. The correct PPE was being worn by the vac work crew during the process.The pipe was suspected to be in poor conditon and works conducted were part of investigation to contribute to design for RAS Pipework output for OP 20 | Type 3 | 2020-08-26 08:10:00 | 1
2020-2021 | INC-0049432 | Finger Point WWTP | Screened waste has been lifted into the screw press and become entangled rather than be moved into the bin. | Type 3 | 2020-09-07 11:03:00 | 1
2020-2021 | INC-0049457 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Ditch #2 DO (sensor) arm out of Mixed Liquor for approx. 15 hours … hence lack of Aeration | Type 3 | 2020-09-10 10:00:00 | 1
2020-2021 | INC-0049479 | Normanville WWTP | As operator arrived to site, emergency storage tank found to be overflowing into | Priority Type 1 | 2020-09-14 12:00:00 | 1
2020-2021 | INC-0049521 | Wirrina Cove WWTP | 1 x 9 kL load of wastewater from Normanville Creek was disposed into Wirrina lagoons before treatment | Type 3 | 2020-09-15 17:00:00 | 1
2020-2021 | INC-0049713 | Christies Beach WWTP | Leaking air valve on Christies Beach to Aldinga Treated Effluent Transfer Pipeline identified by Allwater O&M at approximately 7:00AM on the 05/10/20. Rate of leak approximately 2L/s to stormwater. The pump station was not running. | Type 2 | 2020-10-05 07:00:00 | 1
2020-2021 | INC-0049752 | Naracoorte WWTP (Treatment Works Rd) | Failure of the level sensor meant there was no signal to turn on and off the pumps in the primary pump station. Action by the operator to operate these manually throughout the day prevented a sewerage overflow at the WWTP. | Type 3 | 2020-10-07 09:04:00 | 1
2020-2021 | INC-0049760 | Normanville WWTP | Normanville WWTP: Final Effluent A/C, Locn 93743 E.coli 180 MPN/100mL (Free chlorine 0.1 mg/L, total chlorine 1.9 mg/L) | Type 3 | 2020-10-06 09:00:00 | 1
2020-2021 | INC-0049878 | Finger Point WWTP | Chlorine delivery driver rang to report a bee hive in the chlorine building restricting access and preventing him unloading a drum of chlorine | Type 3 | 2020-10-20 16:25:00 | 1
2020-2021 | INC-0049888 | Port Lincoln WWTP | The onsite storage tank was topped up with chlorinated water and re-circulated to ensure disinfection prior to system being brought back online after winter mode for 6months. A sample was taken and sent to the Labs to ensure water quality. In the meantime a tank in the network was put back online by one of the customers without clearance from SA Water staff, causing the water in the onsite storage tank to be discharged into the network. Labs were contacted immediately to obtain results which indicated that the water was fit for service. | Type 3 | 2020-10-21 16:00:00 | 1
2020-2021 | INC-0049911 | Glenelg Waste Water Treatment Plant | A minor leak (<0.5L/s) has presented from a construction joint in Gallery 10, it has been confirmed that the leak is from the Settled Effluent Pipe. The leak is being contained in the Galleries and there is no offsite discharge. Without further investigation it is unknown as to the extent of the leak below ground and the potential impact to the subsoil. Incident raised as a precautionary Type 2 until further information becomes available. | Type 2 | 2020-10-08 07:30:00 | 1
2020-2021 | INC-0049937 | Finger Point WWTP |  | Type 3 | 2020-10-23 20:00:00 | 1
2020-2021 | INC-0049938 | Port Lincoln WWTP | Failure of both the biogas burners/heaters cause the gas level in the digester to rise to 100%. Neither of the units could be reset and the roof had to be lowered by opening a valve on top of the digester to perform a controlled release of the gas | Type 3 | 2020-10-27 10:50:00 | 1
2020-2021 | INC-0049956 | Whyalla WWTP | Contractor drilling observation bore in roadway hit Whyalla WWTP wastewater water rising main causing leak of raw wastewater to the environment and effluent outfall channel. | Type 2 | 2020-10-29 11:40:00 | 1
2020-2021 | INC-0049968 | Murray Bridge WWTP (Brinkley) | Peats truck carting waste away from site, tailgate came open whilst driving down Pfeiffer Rd and the driver did not realise for approximately 100m. A thin layer of semi-dried sludge has covered 2/3 the width of the road. | Type 3 | 2020-10-30 10:21:00 | 1
2020-2021 | INC-0050012 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Prolonged High Oxygen Demand inflow/Low Reactor DO | Type 3 | 2020-11-03 13:51:00 | 1
2020-2021 | INC-0050027 | Gumeracha WWTP | On routine plant inspection/recording found irrigation pump in fault & not resetting. | Type 3 | 2020-11-03 13:00:00 | 1
2020-2021 | INC-0050029 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | On routine plant visit recording found that a couple of switches in the switchboard at the chemical dosing area had tripped out. | Type 3 | 2020-11-05 07:07:00 | 1
2020-2021 | INC-0050030 | Finger Point WWTP |  | Type 3 | 2020-10-30 07:50:00 | 1
2020-2021 | INC-0050039 | Whyalla WWTP | REVERSED BACK INTO PUMP CAUSING DAMAGE TO REAR BUMPER OF VEHICLE | Type 3 | 2020-11-05 14:20:00 | 1
2020-2021 | INC-0050197 | Normanville WWTP | Normanville WWTP: Poor aeration due to fouled aerators | Type 3 | 2020-11-18 14:49:00 | 1
2020-2021 | INC-0050225 | Millicent WWTP |  | Type 3 | 2020-11-22 18:00:00 | 1
2020-2021 | INC-0050226 | Finger Point WWTP | Power outage at Finger Point yesterday around 230pm for over an hour. When power restored, weirs remained in partially lowered position and cycle did not continue. Operator was called at 10pm and attended site. Aeration basin was very high, no aeration cycle during this period and water was overtopping weirs. Chlorine station was online and functional. | Type 3 | 2020-11-22 22:00:00 | 1
2020-2021 | INC-0050330 | Port Lincoln WWTP | UV disinfection failure caused by a lamp failure of over 10%(6 lamps). on 27/11/20 operators noticed that the number of lamps in fault totalled 5 unknown to the operators at the time an additional 2 lamps where in fault at this time. During a monthly routine check carried out on 30/11/20 the additional 2 lamps where discovered and fixed. TPO notified 1/12/20 and incident was triggered due to confirming we had gone over the limit of 6 failed lamps while still supplying water. | Type 1 | 2020-12-01 09:33:00 | 1
2020-2021 | INC-0050364 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated sludge plant, effluent discharge to creek during summer no flow period, approximately 500 to 720kl discharge after a automated valve returned to the closed position after power outage causing flow to revert to creek | Type 1 | 2020-12-05 10:50:00 | 1
2020-2021 | INC-0050372 | Millicent WWTP | High levels at 96% for Lagoon 1 meant freeboard was not being achieved. With strong winds and rainy conditions predicted for the weekend, this was not a good position and required attention. | Type 3 | 2020-12-05 09:00:00 | 1
2020-2021 | INC-0050393 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2020-12-09 11:30:00 | 1
2020-2021 | INC-0050428 | Finger Point WWTP |  | Type 3 | 2020-12-11 08:00:00 | 1
2020-2021 | INC-0050448 | Gumeracha WWTP | Phone call on the 8th regarding Gumeracha lagoon 2 Hi Hi. Irrigation/reuse control was inhibited on scada due to the forest control switch being turned off, due to this the Reuse to joysons lagoon would not start. | Type 3 | 2020-12-05 11:20:00 | 1
2020-2021 | INC-0050450 | Heathfield WWTP | NOTICE ONLY. UV sampling pump faulted and UV valve failed to close after power failure (also faulted during power reinstating) Due to the failure of the sample pump the UV bypass was enabled and the Chlorine system started running (which its designed to do) so there was constant disinfection at all times. Given the valve to the UV failed to close, the uv system also remained online thus meaning double disinfection partially occurred until I arrived on site. | Type 3 | 2020-12-06 00:00:00 | 1
2020-2021 | INC-0050451 | Wirrina Cove WWTP | Clarifier tank overflow onsite due to Lagoon transfer pumps not being called on via level switches | Type 3 | 2020-12-14 11:35:00 | 1
2020-2021 | INC-0050491 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Turbidity meter on the contact tank faulted at 16:00, Had issues gaining access to SCADA due to INC0252815 access to SA Water network, attended site to see what the issue was. | Type 3 | 2020-12-19 18:30:00 | 1
2020-2021 | INC-0050509 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Generator battery pack has blown up. | Type 3 | 2020-12-21 09:30:00 | 1
2020-2021 | INC-0050713 | Finger Point WWTP | Power failed at the site at 18:15 and the generator for the chlorine dosing failed to start. A plant operator was called and when arrived at site found that the power had returned to normal. Power was off for approx. 75 minutes. | Type 3 | 2021-01-05 18:15:00 | 1
2020-2021 | INC-0050727 | Finger Point WWTP |  | Type 3 | 2021-01-05 19:30:00 | 1
2020-2021 | INC-0050850 | Murray Bridge WWTP (Brinkley) | No indication as to cause or exactly when over the weekend it happened. Obviously the drain became overwhelmed with by volume. This has happened in the past when the sludge silo has particularly watery sludge in it. However Press 2 had been off line for a week or so because of a poly dosing fault so our sludge was really pretty dry as we were only running Press 1 and watching it closely. | Type 3 | 2021-01-04 08:50:00 | 1
2020-2021 | INC-0050883 | Mannum WWTP | Failure of components within Mannum WWTP Irrigation system Request Murray Bridge Workshops to repair asap | Type 3 | 2021-01-21 12:24:00 | 1
2020-2021 | INC-0050913 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2020-2021 | INC-0050915 | Finger Point WWTP | This is the third power outage recorded in the last month, where the plant sequence has been halted and unable to restart without intervention. A request is currently with the workshop to check the PLC program as power outages are frequent at this site, but issues with restarting are relatively new. A generator for this site has been identified for delivery in Plan20. | Type 3 | 2021-01-25 13:09:00 | 1
2020-2021 | INC-0050931 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Low pH inflows causing extended low DOs in both Reactors | Type 3 | 2021-01-28 10:00:00 | 1
2020-2021 | INC-0050979 | Whyalla WWTP |  | Type 2 | 2021-02-02 14:16:00 | 1
2020-2021 | INC-0051049 | Gumeracha WWTP | Control Room contacted myself in regards to a Chlorine Leak Alarm for Gumeracha WWTP whilst I was at Hahndorf WWTP. | Type 3 | 2021-02-09 12:10:00 | 1
2020-2021 | INC-0051129 | Glenelg Waste Water Treatment Plant | Result of E. Coli sample taken 17/2/21 on C/D final effluent A/C sample point 40556 was 980MPN/100mL. Suspected sampling / sampling equipment error, noting the following: grab sample had chlorine residual consistent with previous results (free = 0.5, total = 1.3) and subsequent downstream sample from B Class Effluent tank (source supplied via combined B & C/D effluent) returned E. Coli of 2 MPN/100mL. B Plant Final Effluent A/C result for 17/2/21 was 0 MPN/100mL. | Type 2 | 2021-02-18 13:37:00 | 1
2020-2021 | INC-0051189 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Poor aeration in Ditch #1: High ammonia and BOD in Final A/C Effluent | Type 3 | 2021-02-24 07:30:00 | 1
2020-2021 | INC-0051191 | Myponga Beach WWTP | Myponga Beach WWTP: Irrigation supply (locn 93746): High E.coli 150 orgs/100mL (F 4.1, T 5.0) | Type 3 | 2021-02-09 08:30:00 | 1
2020-2021 | INC-0051355 | Myponga WWTP | Site inspection at WWTP identified a level drop of ~300mm in Lagoon 3, investigation has found a leak at/on the abandoned overflow pipe to the adjacent creek. It is still to be confirmed if the leak is from the pipe itself (i.e. failure of the seal) or if it is leaking around the pipe due to movement of the pipe and/or lagoon bank. | Type 1 | 2021-03-11 10:00:00 | 1
2020-2021 | INC-0051389 | Finger Point WWTP | On low tide last week, plant operator could see grease build up on the outside of the main in multiple locations. On further inspection today, operator observed water and air coming out of main in locations close to the beach. | Type 1 | 2021-03-15 10:30:00 | 1
2020-2021 | INC-0051460 | Mannum WWTP | Mannum WWTP: Irrigation Effluent 290 E.coli/100mL (F 3.4 mg/L, T 5.7 mg/L) | Type 3 | 2021-03-17 00:00:00 | 1
2020-2021 | INC-0051573 | Finger Point WWTP | Small patch of smoke could be seen from the lookout. Potential for concern given windy conditions. | Type 3 | 2021-04-03 15:25:00 | 1
2020-2021 | INC-0051740 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | Leigh Creek WWTP Final Effluent, SP 44902 Microcystis flos-aquae 10800 cells/mL, 18/03/21 | Type 2 | 2021-04-19 16:00:00 | 1
2020-2021 | INC-0051789 | Finger Point WWTP | Operator found central cable on Finger Point Aerator 1 has broken and left aerator unsecured and susceptible to further damage. Aerator 1 is critical to the treatment process. | Type 2 | 2021-04-26 11:27:00 | 1
2020-2021 | INC-0051816 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | Unable to complete training due to no webcam and desktop accessories as well unable to use Ipad to compete training | Type 3 | 2021-04-29 09:14:00 | 1
2020-2021 | INC-0051823 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Brian Thiele a resident on Ambelside road reported to me today by phone that he and his nieghbors have been experiencing Sewer odours for the past 6 weeks | Type 3 | 2021-04-29 15:53:00 | 1
2020-2021 | INC-0051891 | Normanville WWTP | Pre 07/05/2021: Disk Filter system rendered inoperable due to outflow being notably less than the inflow, and was backing up the system, increasing the potential of discharge to the Creek 07/05/2021: Media Filtration system rendered inoperable due to media loss, and agglomeration of solids within the filter manifold | Type 3 | 2021-05-07 10:57:00 | 1
2020-2021 | INC-0051909 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | On Friday Night the VSD faulted (the Device net card) on No1 basins decant drive and couldn't be repaired with the spares on site. This meant the decant to be operated in manual over the weekend. We are continuing to work around the issue and a replacement card is being sauced ASAP. | Type 3 | 2021-05-10 16:11:00 | 1
2020-2021 | INC-0051911 | Mannum WWTP | E.coli 3700 orgs/100mL | Type 1 | 2021-04-12 09:30:00 | 1
2020-2021 | INC-0051945 | Finger Point WWTP |  | Type 3 | 2021-05-14 10:15:00 | 1
2020-2021 | INC-0051946 | Finger Point WWTP |  | Type 3 | 2021-05-14 10:23:00 | 1
2020-2021 | INC-0052000 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Severe sewer odour affecting the whole town of Pt Pirie. Issue being caused by a failure at the WWTP. Issue is being worked on by electricians. | Type 2 | 2021-05-21 16:49:00 | 1
2020-2021 | INC-0052043 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2021-05-22 09:10:00 | 1
2020-2021 | INC-0052052 | Bolivar High Salinity Waste Water Treatment Plant | Resident reported that trucks were driving along internal north south dirt road, creating dust that was blowing over northern connector expressway and to the residents home. Normally road is watered for dust suppression but presumably this had been overlooked this day perhaps as it was a weekend. | Type 3 | 2021-05-22 15:14:00 | 1
2020-2021 | INC-0052053 | Mannum WWTP | Mannum Lagoon WWTP (River Lane): Vacuum regulator failure on auto-changeover: Non disinfected Effluent (approx 40kL) discharged to Mannum GC | Type 2 | 2021-05-28 05:15:00 | 1
2020-2021 | INC-0052301 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Biomass in SBR 1 and SBR 2 has died due to loss in aeration. | Type 3 | 2021-06-23 14:00:00 | 1
2020-2021 | INC-0052315 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2020-2021 | INC-0052382 | Angaston WWTP | AWQC lab testing reported a BOD of 31mg/L, this is in excess of the 20mg/L. The incident has been classified as a Type 3 as while this is high, the annual median is below the compliance requirement of 20 mg/L | Type 3 | 2021-06-17 00:00:00 | 1
2020-2021 | INC-0052946 | Normanville WWTP | Feedback submitted via Customer advocate regarding odour from Normanville WWTP. Odour is associated with the change to single basin operation (holding wastewater in emergency storage) required to undertake maintenance and inspection of SBR. | Type 3 | 2021-06-10 09:35:00 | 1
2021-2022 | INC-0052395 | Finger Point WWTP | Sump pumps are inadequate for hardstand size. OIR has already been raised. Compounded by wet sludge issues and potential for sludge to be returned to head of the plant. | Type 2 | 2021-07-02 09:08:00 | 1
2021-2022 | INC-0052424 | Finger Point WWTP | Plant operator received call from the control centre regarding a 'sequence failed to start' alarm. This intermittent fault has occurred on a number of occasions in the past 6 months but has been unable to be diagnosed after the event. PLC program stuck in decant mode. Storm cycle was not initiated, but the level in the basin was so high, it was passing over the weirs at full height. Loss of treatment process for a full aeration cycle occurred and carry over of solids into the polishing lagoons on restart due to excessive flows/rate. | Type 3 | 2021-07-06 18:30:00 | 1
2021-2022 | INC-0052489 | Victor Harbor (Boot) WWTP | 3 inch pipe service water main split, discharging from approximately 0930 to 1130 of approximately 30-40kL. The water has been chlorinated and UV treated. It was flowing in the direction of the Inman River and determined to be worst case scenario that some may have made it into the water course. The water course in question is one that TRILITY are licensed to discharge into for defined periods the year. | Type 2 | 2021-07-15 13:40:00 | 1
2021-2022 | INC-0052511 | Gumeracha WWTP |  | Type 1 | 2021-07-19 08:00:00 | 1
2021-2022 | INC-0052520 | Finger Point WWTP | Supernatant and underdrain systems also backed up and at capacity. | Type 3 | 2021-07-19 21:28:00 | 1
2021-2022 | INC-0052602 | Mount Burr WWTP | Exposed trees are falling over in high wind conditions experienced over the weekend as protection from the forest has now gone. Trees have fallen across roadways near the imhoff tank. Roadways that have been used by heavy vehicles are now in poor condition and are slippery, requiring 4WD to access. | Type 3 | 2021-07-26 09:00:00 | 1
2021-2022 | INC-0052603 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Plant instability due to inability to use Swing Zone in Reactor A, unable to use PID control for Blower ops and multiple power outages over weekend | Type 3 | 2021-07-26 11:00:00 | 1
2021-2022 | INC-0052650 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): (Old) Sludge Lagoon overflowed a combination of Arris (Septic Tank) Effluent and Stormwater to Hahndorf Creek | Type 2 | 2021-07-29 15:31:00 | 1
2021-2022 | INC-0052660 | Millicent WWTP | Infiltration in the network occurs each year and booster pump was switched on yesterday to cope with high levels in No1 Pump station. Recent rainfall events have caused groundwater to rise above sewer main pipework levels resulting in infiltration. Infiltration will now occur until later in the year when groundwater levels recede. | Type 3 | 2021-07-30 15:05:00 | 1
2021-2022 | INC-0052713 | Mannum WWTP | One of 2 pipes connected during recent works were found to be leaking by Murray Bridge Workshop staff. Sewage was found to be flowing from the Imhoff Tank, down the steps, past the office and into the offline sludge lagoon. Workshops called on-call Operator who attended site and confirmed leak. No visible water was in the sludge lagoon with minor erosion evident due to flow of water. | Type 3 | 2021-08-06 15:28:00 | 1
2021-2022 | INC-0052754 | Port Lincoln WWTP | Both RSPs showed high inlet pressure earlier today, corrective action was undertaken to reduce flow into the RSPs (flow reduction 0.6 to 0.5 L/S). Process was maintained through-out the day. Operator noticed issues when performing other duties and reported Loading Bay 2 was caked in un-dried solids. This caused the slightly thickened sludge to slouch and run. | Type 3 | 2021-08-10 13:55:00 | 1
2021-2022 | INC-0052811 | Finger Point WWTP | Rag material comes through to the plant in large mats/balls and overwhelms the screen, leading to the screen to be bypassed while the screen is cleared and normal operation can continue. Bypassing the screens, results in rag material entering the aeration basin, impacting on performance and downstream processes. | Type 3 | 2021-08-16 09:00:00 | 1
2021-2022 | INC-0052829 | Naracoorte WWTP (Treatment Works Rd) | Plant operator noticed that the screen was blocked and not operational. Resetting would not start the screen and on further investigation found the level sensors to be faulty. | Type 3 | 2021-08-19 12:01:00 | 1
2021-2022 | INC-0052857 | Finger Point WWTP | Rag material comes through to the plant in large mats/balls and overwhelms the screen, leading to the screen to be bypassed while the screen is cleared and normal operation can continue. Bypassing the screens, results in rag material entering the aeration basin, impacting on performance and downstream processes. The operator also noticed that there are spacers missing from the step screen. The spacers/fingers help the material be lifted into the screw press. | Type 3 | 2021-08-23 08:00:00 | 1
2021-2022 | INC-0052859 | Wirrina Cove WWTP | Wirrina Cove WWTP: On site flood contained within containment bund Effluent disposal pump failed to operate, system would push effluent to storage Lagoons, excess effluent flooded area within containment bund | Type 3 | 2021-08-24 09:00:00 | 1
2021-2022 | INC-0052886 | Naracoorte WWTP (Treatment Works Rd) | Police security contacted WWTC to notify of security alarm at the WWTP. The security system has been faulting multiple times this week where it has had to be reset. | Type 3 | 2021-08-26 15:45:00 | 1
2021-2022 | INC-0052921 | Finger Point WWTP | During routine sampling and activities, the plant operator noticed the sewage was black coming into the plant. While sewage can tend to be dark in colour due to the 2 day resident time in the main from Mount Gambier, this was colour was very unusual. No online monitoring at the plant or No1 Pump station so events are very hard to detect. Impact to single basin will be monitored. | Type 3 | 2021-08-30 08:45:00 | 1
2021-2022 | INC-0053001 | Angaston WWTP | We discovered a 1 metre piece of asbestos pipe at the Angaston WWTP spoil dumping area which was not wrapped. It is not clear on how the piece of pipe ended up there or how long it was sitting there. | Type 3 | 2021-09-07 13:15:00 | 1
2021-2022 | INC-0053067 | Finger Point WWTP | The operator noticed that sewage was dribbling out of the bypass pipe a few hours after completing a PM task to open another bypass valves and flush built up debris through to the polishing lagoons. When checking the inlet screens, he noticed that there was a huge build up of rag material and at that time, the high level alarm was activated. | Type 3 | 2021-09-14 09:47:00 | 1
2021-2022 | INC-0053077 | Port Lincoln WWTP | Basin 2 storm cycle, No Rain or storm event . sunny day | Type 3 | 2021-09-17 10:17:00 | 1
2021-2022 | INC-0053116 | Bolivar High Salinity Waste Water Treatment Plant | WWTP switched to back-up power supply at approximately 7am on 21/9/21 to facilitate planned ZCEF integration works on the primary supply. As part of this a backup generator was installed at PEPS to supply power to the station (no direct supply when on back-up feeder). Complications with the PEPS generator/pumps occurred which reduced the capacity of PEPS and with plant inflows exceeding the PEPS capacity excess flows overflowed directly to the stabilisation lagoons between 11:15am and 5pm. A subsequent generator fault at approximately 1:30am 22/9/21 also resulted in a second minor bypass event for a duration of approximately 15 minutes. Estimated total volume bypassed to lagoons form both events is 11.25ML. | Type 2 | 2021-09-21 11:15:00 | 1
2021-2022 | INC-0053129 | Finger Point WWTP | Magflo meter in discharge pipe is original 30 year old flow meter and needs replacing (OIR). Pipework type (Ribloc) and valving is preventing this from occurring at this stage. Temporary strap on flow meter that was installed approx 10years ago as a back up, in now functioning as the primary flow meter, but it being influenced by the air when the flow drops below around 130L/sec. It then takes 20-30minutes to recover and resume chlorine dosing (flow paced). | Type 3 | 2021-09-21 10:01:00 | 1
2021-2022 | INC-0053142 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Rain Water Supply, SP42794: 13/09/2021 E.coli 1 org/100mL | Type 3 | 2021-09-22 11:00:00 | 1
2021-2022 | INC-0053181 | Port Lincoln WWTP | Daily inflow caused storm cycle. NO RAIN | Type 3 | 2021-09-27 13:35:00 | 1
2021-2022 | INC-0053255 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2021-10-02 09:00:00 | 1
2021-2022 | INC-0053256 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2021-10-05 08:00:00 | 1
2021-2022 | INC-0053270 | Finger Point WWTP | Build up of solids in single drainage channel that is undersized for the catchment area. Build up of solids in channel as a result of contractors working on wet biosolids and hosing off heavy fleet. Grid mesh is bolted down and bolts have seized, so making cleaning difficult. | Type 3 | 2021-10-06 18:30:00 | 1
2021-2022 | INC-0053272 | Port Lincoln WWTP |  | Type 3 | 2021-10-07 09:33:00 | 1
2021-2022 | INC-0053296 | Port Lincoln WWTP | Weir 3 failed (basin 2) to operate. lack of comms . caused plant to run in single basin operation on B1 . No Alarms to indicate fault | Type 3 | 2021-10-11 08:23:00 | 1
2021-2022 | INC-0053327 | Port Lincoln WWTP | Basin 1 storm cycle caused by return flow from sludge handling and light rain. | Type 3 | 2021-10-14 10:03:00 | 1
2021-2022 | INC-0053335 | Port Lincoln WWTP | Power flick causing aeration basins to reset process timers. aeration time had to be manually adjusted to bring basins back to regular timing. | Type 3 | 2021-10-13 08:04:00 | 1
2021-2022 | INC-0053339 | Port Lincoln WWTP | Weir 3 actuator faulted but did not alarm, this caused the program to continue to operate but basin 2 was not usable during this time. Basin 1 was operating as the sole aeration basin until 11/10/21 8:00 when the problem was noticed by operators. Reuse supply was stopped on 12/10/21 due to high turbidity. Council notified and will reassess later in the week to see if this can be put back online. | Type 3 | 2021-10-10 05:30:00 | 1
2021-2022 | INC-0053375 | Port Lincoln WWTP | PLC for WWTP crashed around 2am, site was attended by electricians to repair. Comms failure between AS plant and Sludge Handling. Basins in repeat mode (SBR 1 high level by 8am, manual intervention required). Sludge handling not visible in office. | Type 2 | 2021-10-19 07:45:00 | 1
2021-2022 | INC-0053424 | Glenelg Waste Water Treatment Plant | 170 MPN/100mL Limit is > 100 <= 400 MPN/100mL Prod Spec: Restricted_RW_ASP | Type 3 | 2021-10-22 05:00:00 | 1
2021-2022 | INC-0053452 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2021-2022 | INC-0053460 | Finger Point WWTP | Plant operator was slashing fire tracks and on return noticed dripping of hydraulic oil after getting out of the tractor. | Type 3 | 2021-10-26 13:00:00 | 1
2021-2022 | INC-0053466 | Port Lincoln WWTP | Raw feed isolation switch floods when we higher tides cause a electrical fault causing a water supply issue to council. switch is currently located in a water water sump where is wet a humid and a confined space covered by very heavy concrete lids, making it not a simple fix. switch needs to be moved to above ground making easier safer access . | Type 3 | 2021-10-27 07:57:00 | 1
2021-2022 | INC-0053489 | Gumeracha WWTP | NOTIFICATION OF INCIDENT Storm front come through with large hail about the size of a golf ball causing damage to the bonnet and roof of vehicle S304AQZ | Type 3 | 2021-10-28 12:00:00 | 1
2021-2022 | INC-0053502 | Port Lincoln WWTP | WWRPS Faulted and shut down due to Low flow deviation , this happened with high in coming flow from the network. | Type 3 | 2021-10-26 13:00:00 | 1
2021-2022 | INC-0053503 | Port Lincoln WWTP | WWRPS faulted and shut down due to low flow deviation alarm. this seems to happen with high network inflows. appears pump station struggles to pump against incoming network flow. something to keep in mind when the grit and screens upgrade comes to the table. | Type 3 | 2021-10-28 10:12:00 | 1
2021-2022 | INC-0053529 | Port Lincoln WWTP | WWRPS low flow deviation alarm due to high incoming flow , caused pump station to shut down then overflow to emergency sludge lagoon | Type 3 | 2021-11-01 10:22:00 | 1
2021-2022 | INC-0053530 | Port Lincoln WWTP | WWRPS Low flow deviation alarm. number 2 for the day . shutting down the WWRPS | Type 3 | 2021-11-01 10:34:00 | 1
2021-2022 | INC-0053542 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Inlet low pH (pH 5.0) | Type 3 | 2021-11-02 08:00:00 | 1
2021-2022 | INC-0053586 | Glenelg Waste Water Treatment Plant | 260 MPN/100mL Limit is > 100 <= 400 MPN/100mL Prod Spec: Restricted_RW_ASP | Type 3 | 2021-11-05 10:00:00 | 1
2021-2022 | INC-0053654 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2021-2022 | INC-0053655 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) |  | Type 3 | 2021-11-11 16:18:00 | 1
2021-2022 | INC-0053657 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Ditch #1 High ammonia (>8 mg/L) due to poor aeration | Type 3 | 2021-11-11 16:22:00 | 1
2021-2022 | INC-0053703 | Port Lincoln WWTP | Storm Cycles in Basin 1 Triggered with no rain event occurring in the network | Type 3 | 2021-11-17 13:23:00 | 1
2021-2022 | INC-0053719 | Port Lincoln WWTP | Storm Cycle Basin 1 with no rain event occurring in the catchment network | Type 3 | 2021-11-18 13:22:00 | 1
2021-2022 | INC-0053778 | Port Lincoln WWTP | Step screen in the grit and screen failed , motor failed new one ordered . | Type 3 | 2021-11-19 09:53:00 | 1
2021-2022 | INC-0053779 | Port Lincoln WWTP | WAS pump station pump 2 choked up with large amounts of rag | Type 3 | 2021-11-24 09:57:00 | 1
2021-2022 | INC-0053782 | Whyalla WWTP | Due to high rainfall and low evaporation rates level in WWTP lagoon 7 has increased due to the lagoon discharge having been ceased in late October. Environmental flows with initiated to reduce the level. | Type 3 | 2021-11-24 14:50:00 | 1
2021-2022 | INC-0053818 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird-In-Hand WWTP: High Oxygen Demand inflow | Type 3 | 2021-11-23 08:30:00 | 1
2021-2022 | INC-0053831 | Finger Point WWTP | When heavy rag loads go through the step screen the screw press trough seems to build up so high the rag can no longer drop off the step screen into the trough. If the rag does not drop off the end bar into the trough the moveable bars catch it and drag it into the plastic fingers where it continues to build up. | Type 3 | 2021-11-29 08:50:00 | 1
2021-2022 | INC-0053840 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Low pH and High Oxygen Demand Inflows | Type 3 | 2021-11-30 12:00:00 | 1
2021-2022 | INC-0053878 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): High Oxygen Demand Inflow: Activated Sludge Reactors 2 and 3 | Type 3 | 2021-12-05 19:30:00 | 1
2021-2022 | INC-0053879 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Numerous High Oxygen Demand Inflows weekend of 04/12/2021 | Type 3 | 2021-12-05 19:45:00 | 1
2021-2022 | INC-0053880 | Naracoorte WWTP (Treatment Works Rd) | Blockages have occurred on Thursday 2nd and Saturday 4th December. Settled grit has also been seen dislodging from the bottom and pass through the system. Cleaning out of the grit chamber occurred 2 weeks prior and it is unusual for the plant to be still seeing these events. Grit chamber solids removed were particularly odourous and still have some remaining odour in sludge bed. | Type 3 | 2021-12-04 07:00:00 | 1
2021-2022 | INC-0053913 | Port Lincoln WWTP | Sludge Dewatering occurring without polymer dosing for approx 10min. Please see attached email for full detail | Type 3 | 2021-12-03 12:00:00 | 1
2021-2022 | INC-0053926 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2021-12-09 11:30:00 | 1
2021-2022 | INC-0053935 | Port Augusta Prison WWTP | Floating sludge has caused the transfer lines to be partially blocked. | Type 3 | 2021-12-13 07:56:00 | 1
2021-2022 | INC-0053991 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): UVT <40% | Type 3 | 2021-12-16 09:04:00 | 1
2021-2022 | INC-0054004 | Finger Point WWTP | Blockages occurred on same day, one at 8am the other around 12pm, each of approximately a wheel barrow full. | Type 3 | 2021-12-16 12:01:00 | 1
2021-2022 | INC-0054055 | Port Lincoln WWTP | Tail gate of a contractor trailer transporting biosolids from Port Lincoln failed during transport. This caused the biosolids to be lost across a public road (map attached) | Type 1 | 2021-12-22 09:18:00 | 1
2021-2022 | INC-0054092 | Port Lincoln WWTP | WWRPS went into low flow alarm and shut down due high incoming network flows . | Type 3 | 2021-12-24 12:41:00 | 1
2021-2022 | INC-0054100 | Port Lincoln WWTP | A power outage in the local area caused power to the WWTP to be lost. Oncall attendance was provided. Power was restored to site approx 8:15am. Electrician onsite reset all faults, however Aerator 3 and reuse turbidity meter failed to restart. - Aerator 3: this was left offline, and will be attended to on the next business day (Wednesday 29/12/21) - Reuse turbidity meter: As this is critical to the reuse plant and was only displaying local information (no connection to the PLC), the reuse tank was filled and the reuse plant shut down as no online monitoring was possible. Council informed of this. | Type 3 | 2021-12-25 08:00:00 | 1
2021-2022 | INC-0054114 | Port Lincoln WWTP | Transmittance meter faulted during power outage on the 25/12/21 , meter will need outside repairs to be done | Type 3 | 2021-12-29 13:09:00 | 1
2021-2022 | INC-0054116 | Finger Point WWTP |  | Type 3 | 2021-12-28 09:00:00 | 1
2021-2022 | INC-0054136 | Finger Point WWTP | Material coming into plant is overwhelming the screen and usual sensors are not working optimally. Build up of material in the screw auger has led to it overflowing onto ground in bunded area and walkways. Screen is requiring a lot of manual intervention by operator, which has not been possible over Christmas. | Type 3 | 2021-12-31 11:30:00 | 1
2021-2022 | INC-0054184 | Finger Point WWTP | The screen UPS failed taking out the screen system, closing the screen inlet valve and sewage flowing out through the bypass valve unscreened into the aeration basin. Electrician received call from control centre to attend to site. Electrician has also noted that both the level sensor and float has faulted and are no longer working. | Type 3 | 2022-01-05 16:15:00 | 1
2021-2022 | INC-0054215 | Victor Harbor (Boot) WWTP | Customer contacted TRILITY and said that the smell has been strong for the last 5 hours. Stated that there is little wind movement and it's a problem for them; even the garden vegetables have a film of the stench on them. TRILITY Operations Manager Fleurieu informed IM that there were no biosolids movements on 06/01/22 i.e. no offsite movement or sludge removal from lagoons due to still being in the holiday period and noted the customer's comment on minimal wind movement which reduces the probability that the Victor Harbor Plant as the odour source. Other potential odour source might be septic tank, neighbouring paddock etc. IM was informed that Plant Process Controllers have conducted a repeat odour test (on 07/01/22) at the site boundary and Panorama Drive on 07/01/22 morning and that there no odour present. | Type 3 | 2022-01-06 16:53:00 | 1
2021-2022 | INC-0054254 | Port Lincoln WWTP | Weir encoder Fault 1,2,3 and 4. all weirs faulted out causing basins 1 and 2 to fault and reset to 0 | Type 3 | 2022-01-11 11:09:00 | 1
2021-2022 | INC-0054262 | Port Lincoln WWTP | reuse was shutdown due to a build up of horse algae blocking the inlet screen . something needs to be done about this ongoing issue | Type 3 | 2022-01-12 10:35:00 | 1
2021-2022 | INC-0054338 | Finger Point WWTP | 4WD driver called call centre to ask for assistance to get off beach. Unfamiliar with area and tides and very apologetic. | Type 3 | 2022-01-18 14:20:00 | 1
2021-2022 | INC-0054354 | Naracoorte WWTP (Treatment Works Rd) | Operator noticed white discharge for the second day in a row around 730am. He was unable to get a sample on the first day due to timing of the discharge and did not know how long it may have occurred. This event went for about an hour and a half and turned the inlet works white, with an odour similar to glue. Unaware of any regular activities in Naracoorte that have the potential to cause this issue. | Type 3 | 2022-01-20 07:30:00 | 1
2021-2022 | INC-0054379 | Whyalla WWTP | Due to low evaporation rates water level has resulting in an overall increasing in the WWTP level. With high rainfall expected over the weekend this would increase | Type 3 | 2022-01-20 09:59:00 | 1
2021-2022 | INC-0054390 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | Due to the high rainfall over the weekend, Operators have expressed concern that there may have been overflow from Lagoon 3 to the environment. Lagoon 3 contains water which has already been processed by 2 aerated lagoons and is a holding lagoon prior to disinfection for reuse. Due to the volume of water present (as rainfall ~110mm) in the area, any overflow would be highly diluted. | Type 2 | 2022-01-24 10:15:00 | 1
2021-2022 | INC-0054391 | Port Lincoln WWTP | Waste water return pump station low flow deviation alarm due to high incoming network flows 113 ltr/sec with NO Rain , this faults pump station and needs to reset before it will pump again. if not caught can overflow into emergency lagoon | Type 3 | 2022-01-24 10:35:00 | 1
2021-2022 | INC-0054392 | Port Lincoln WWTP | Weir 1 encoder fault , needing on call to attend site to reset | Type 3 | 2022-01-24 10:46:00 | 1
2021-2022 | INC-0054402 | Murray Bridge WWTP | Surfactant rich influent impacted plant process at Murray Bridge WWTP Brinkley causing the UVT to drop low enough that the UV system went into auto shutdown. With this in mind John Holland were unable to send water over to the Army Wetlands undisinfected. It was a necessity that the plant was able to send this water elsewhere to get rid of the poorer treated wastewater and avoid the onsite lagoons overflowing. The options of controlled discharge to the swale area behind the plant and to the old WWTP lagoons were discussed and consulted with Mike O'Brien. It was decided that a controlled release to the old WWTP lagoons of approx 10ML was the best option, having little impact to the old lagoons water quality. | Type 3 | 2022-01-21 08:30:00 | 1
2021-2022 | INC-0054403 | Murray Bridge WWTP (Brinkley) | Surfactant rich influent with a low pH impacted plant process at Murray Bridge WWTP Brinkley causing the UVT to drop low enough that the UV system went into auto shutdown. When such discharge comes in, the media tends to float and not circulate as it retains foam within the plastic media. We have noticed this happening a lot over the December & January period. There have been many, many low pH detection and foaming observed but they tend to be quite transient and not prolonged like the two below. With this in mind John Holland were unable to send water over to the Army Wetlands undisinfected. It was a necessity that the plant was able to send this water elsewhere to get rid of the poorer treated wastewater and avoid the onsite lagoons overflowing. The options of controlled discharge to the swale area behind the plant and to the old WWTP lagoons were discussed and consulted with Mike O'Brien. It was decided that a controlled release to the old WWTP lagoons of approx 10ML was the best option, having little impact to the old lagoons water quality. | Type 3 | 2022-01-21 08:55:00 | 1
2021-2022 | INC-0054404 | Port Lincoln WWTP | WWRPS low flow deviation alarm , causing pump station to shut down needing to be reset. NO Rain, caused by network inflow 104 ltrs/sec . if not reset station will overflow into emergency lagoon | Type 3 | 2022-01-25 09:29:00 | 1
2021-2022 | INC-0054405 | Port Lincoln WWTP | Dewatering/Thickening polymer was batched incorrectly. SCADA control showed the correct dose rates (0.75 and 1.0%) however the concentration control screen on both Prominent polymer batching units showed 0.5%. This resulted in batch strength of the polymer being significantly less that required and ineffective dewatering/thickening occuring. Further investigation showed the system had also entered weekend mode, which stops polymer batching | Type 3 | 2022-01-25 11:50:00 | 1
2021-2022 | INC-0054436 | Port Lincoln WWTP | The thickener poly batching pump for some reason started to pump again after about an hour to an hour and a 1/2 of the last poly batch being made up. This means the poly pump ran by itself with no white pump running indicator on SCADA. This occurred at 2pm and continued until around 6pm when oncall electricians attended site due to high high alarm on polymer batching system, they called the on-call operator (Matt Stockham). | Type 3 | 2022-01-26 18:26:00 | 1
2021-2022 | INC-0054447 | Millicent WWTP | Lagoon 2 and 3 screens are ineffective due to condition, causing the inline filter prior to the pump to constantly block. While the inline pot filter is being cleaned daily, the farmer is unable to run the pivot for a full circle before loosing pressure and the system shutting down. A maintenance request has previously been submitted to repair/replace the screens. | Type 3 | 2022-01-25 08:59:00 | 1
2021-2022 | INC-0054453 | Murray Bridge WWTP (Brinkley) |  | Type 2 | 2022-01-28 12:10:00 | 1
2021-2022 | INC-0054489 | Normanville WWTP | Normanville WWTP Final Effluent A/C SP93743 E.coli 200/100mL | Type 3 | 2022-01-06 09:30:00 | 1
2021-2022 | INC-0054514 | Port Lincoln WWTP | Whilst reversing out of a car park , turned to soon and hit a white bollard denting front right quarter panel and scratched bumper . Not bad ute still driveable | Type 3 | 2022-02-02 09:44:00 | 1
2021-2022 | INC-0054536 | Port Lincoln WWTP | was feed pump to RDT 1 fault . drawing high amps indicating pump is choked . suspected rag | Type 3 | 2022-02-03 18:00:00 | 1
2021-2022 | INC-0054559 | Port Augusta West WWTP | This is the second time in a week that an oily material has been dumped in these bays. This material is not suitable for the area and will contaminate a large area of the lagoon. Pictures attached. | Type 2 | 2022-02-07 08:20:00 | 1
2021-2022 | INC-0054575 | Port Lincoln WWTP |  | Type 3 | 2022-02-08 09:12:00 | 1
2021-2022 | INC-0054581 | Naracoorte WWTP (Treatment Works Rd) | As above | Type 3 | 2022-02-08 09:00:00 | 1
2021-2022 | INC-0054599 | Port Lincoln WWTP | WWRPS faulted on low flow alarm, faulting and shutting down due high incoming network flows 109 ltr/sec. No Rain . | Type 3 | 2022-02-10 10:19:00 | 1
2021-2022 | INC-0054607 | Port Lincoln WWTP | WWRPS Low flow fault causing pump station to shut down until reset due high incoming network flows . incoming flow 96 ltr/sec NO rain | Type 3 | 2022-02-11 09:00:00 | 1
2021-2022 | INC-0054619 | Finger Point WWTP | Sludge coming into the inlet screen is being taken up by the step screen and once in the screw press it is unable to be moved across to the bin. Temporary washers added to alleviate the issue work well, but drain the wash water tank and need to be connected to the signal which moves the step screen up via a solenoid valve. Sludge has been detected in the headworks since just before Christmas. Trade Waste have been notified of changes. | Type 3 | 2022-02-11 11:30:00 | 1
2021-2022 | INC-0054627 | Port Lincoln WWTP | WWRPS Low flow fault causing pump station to shut down until reset due high incoming network flows . incoming flow 105 ltr/sec NO rain | Type 3 | 2022-02-14 08:41:00 | 1
2021-2022 | INC-0054664 | Port Lincoln WWTP | Aeration basin overflow due to rain , high incoming flows of upto 130 ltr/sec. no water quality issues | Type 3 | 2022-02-16 11:20:00 | 1
2021-2022 | INC-0054757 | Port Lincoln WWTP | WWRPS low flow alarm causing pump station to fault and not run . incoming flow 107 ltr/sec with low flow alarm delay already increased to 45 sec | Type 3 | 2022-02-23 09:57:00 | 1
2021-2022 | INC-0054794 | Christies Beach WWTP | crew were working within the DN1200 incoming line last night 24/02, and one of tubs of equipment strapped to a team member has unravelled and been lost down the line between 2-3am. The large blue tub (0.5m x 0.5m) was located in a nearby downstream manhole from where our works finish and the 2 x milwaukee drill power tools were not located, either in the line or in the inlet screens. | Type 3 | 2022-02-25 15:41:00 | 1
2021-2022 | INC-0054825 | Port Lincoln WWTP | Pump 1 faulted due to ragging Pump 2 faulted due to cable being ripped out, chain was also pulled from housing WAS mixer faulted due to chain and cable of Pump 2 being wrapped around mixer blades Pump 2 removed from guiderails and lodged under bottom mixer blades of mixing shaft | Type 3 | 2022-03-01 14:00:00 | 1
2021-2022 | INC-0054837 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2021-2022 | INC-0054905 | Port Lincoln WWTP | Dewatering Polymer batching plant shutdown caused by a "Pump maximum reached" fault. batching unit continues to batch the plant but will not run automatically until the fault has been reset. | Type 3 | 2022-03-09 09:00:00 | 1
2021-2022 | INC-0054930 | Millicent WWTP | On investigation found an overturned vehicle that had caught the paddock on fire to the south of the WWTP on adjoining land (Croser - SAW's recycled water user). Two council workers had also seen smoke and had reported vehicle to emergency services. Occupants known to police and had walked away unharmed from vehicle. Farmer and fire vehicles were in attendance when operator left. Millicent WWTP has only one entry/exit route, so vigilance is required in summer. | Type 3 | 2022-03-11 13:21:00 | 1
2021-2022 | INC-0054938 | Finger Point WWTP | Screen unable to lift the material and was rolling at the bottom of the step screen. Sludge had made its way up into the screw press and had overflowed. | Type 3 | 2022-03-14 07:00:00 | 1
2021-2022 | INC-0054959 | Finger Point WWTP | While not as large as the 2 previous events earlier in the week, the material was sufficient that the screen was unable to be lifted by the step screen and was rolling around at the bottom, causing a partial blockage. | Type 3 | 2022-03-16 11:56:00 | 1
2021-2022 | INC-0054960 | Port Lincoln WWTP | Waste water return pump station low flow alarm . network flows 100 ltr/sec with rain . pump stations faults and shuts down . potential onsite overflow if not restarted | Type 3 | 2022-03-16 13:22:00 | 1
2021-2022 | INC-0054992 | Port Lincoln WWTP | WWRPS low flow alarm due high incoming network flows 103lts/sec, pump stations faults and will not start until its is reset. possible overflow of pump station | Type 3 | 2022-03-21 09:30:00 | 1
2021-2022 | INC-0055001 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2022-03-21 12:00:00 | 1
2021-2022 | INC-0055027 | Port Lincoln WWTP | Strong odour coming from aeration basins while aerating. Odour increased in intensity over the morning | Type 3 | 2022-03-24 08:00:00 | 1
2021-2022 | INC-0055031 | Port Lincoln WWTP | WWRPS low flow alarm , network inflow of 109ltr sec. pumps station faulted and if not reset in time it will overflow | Type 3 | 2022-03-24 12:54:00 | 1
2021-2022 | INC-0055054 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2021-2022 | INC-0055071 | Finger Point WWTP | Oncall plant operator got a call regarding a soft starter fault. On checking the plant this morning, saw that Aerator 2 had broken free of its moorings and damaged hand rails and cable trays. Further inspection is required. Aerator 2 is a critical aerator and will impact plants treatment capability. Cables regularly fail and identified improvements have not been able to be implemented due to being unable to empty the single treatment basin. | Type 3 | 2022-03-28 07:25:00 | 1
2021-2022 | INC-0055076 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Aeration system not isolating when basins are switched over, this has resulted in the basins loosing biomass over the weir during decant. Additionally, this has seen a detrimental effect on the opposite basin resulting in ineffective aeration | Type 3 | 2022-03-27 11:13:00 | 1
2021-2022 | INC-0055093 | Port Lincoln WWTP | wwrps low flow alarm , shutting pump station down | Type 3 | 2022-03-29 13:42:00 | 1
2021-2022 | INC-0055111 | Port Lincoln WWTP | WWRPS low flow alarm shutting down pump station. high network flows | Type 3 | 2022-03-30 10:18:00 | 1
2021-2022 | INC-0055121 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Ammonia >8 mg/L in Final Effluent | Type 3 | 2022-03-30 09:00:00 | 1
2021-2022 | INC-0055125 | Finger Point WWTP |  | Type 3 | 2022-03-30 14:20:00 | 1
2021-2022 | INC-0055133 | Victor Harbor (Boot) WWTP | The fire appears to have started during planned grass mowing of the firebreak being conducted by an external contractor. No damage to WWTP infrastructure, machinery or personnel. CFS contacted and extinguished the fire with water and fire retardant. The total burnt area is estimated to be approximately 150m2 and 20 km/h winds blowing away from the WWTP were reported at the time of the incident. An incident investigation will be completed in coming days and this stage a root cause is not know. | Type 3 | 2022-03-30 16:24:00 | 1
2021-2022 | INC-0055181 | Port Lincoln WWTP | WWRPS faulted on low flow , shutting pump station down . incoming flow 89 ltr sec | Type 3 | 2022-04-03 12:17:00 | 1
2021-2022 | INC-0055182 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): UV system Ballast Failure 03/04/2022 | Type 3 | 2022-04-03 08:30:00 | 1
2021-2022 | INC-0055191 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Polymer Storage, failure of polymer lines resulting in a <500L Zetag 9146FS spill into bunded/catchment area, and process | Type 3 | 2022-04-05 10:03:00 | 1
2021-2022 | INC-0055205 | Port Lincoln WWTP | WWRPS faulted on low flow causing station not to pump , operations were not notified causing overflow onsite . network flows 88 ltr sec | Type 3 | 2022-04-05 15:21:00 | 1
2021-2022 | INC-0055248 | Port Lincoln WWTP | Front gate failed to open , checked all power was on. found security control box at the Gate full full full of Mini Ants . | Type 3 | 2022-04-08 08:12:00 | 1
2021-2022 | INC-0055274 | Angaston WWTP | Angaston Lagoon WWTP (Stockwell Rd): Chlorine Dosing Station: Chlorine Gas leak detected within cylinder storage/dosing room | Type 2 | 2022-04-12 04:30:00 | 1
2021-2022 | INC-0055280 | Finger Point WWTP | Tow truck operator would not access the vehicle through the beach public access road, so owner of vehicle pulled it up to the SAW gate instead. Car unable to be moved without assistance. | Type 3 | 2022-04-12 14:00:00 | 1
2021-2022 | INC-0055288 | Naracoorte WWTP (Treatment Works Rd) | Plant operator on Saturday was unable to properly waste sludge from the primary sedimentation tanks. When doing this daily task the following day, it required significant effort to unblock but was successful. Thickness of sludge has been an issue for a few months and operator has had to use several methods to unblock. | Type 3 | 2022-04-10 07:00:00 | 1
2021-2022 | INC-0055296 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): High Reactor A and C Mixed Liquors Due to a number of factors, the Mixed Liquor in Reactors A and C is very high, greater than high level operational limits ... this is due to: - Concentration of MLSS by a recent polymer spill into the process returns - Inability to have bins emptied due to contractor frequencies - Increase in SS loads from Network TW contributors | Type 3 | 2022-04-13 13:42:00 | 1
2021-2022 | INC-0055349 | Port Lincoln WWTP | WWRPS low flow alarm causing pump station to fault and reach high sump level shutting down processing | Type 3 | 2022-04-20 14:44:00 | 1
2021-2022 | INC-0055350 | Port Lincoln WWTP | WWRPS low flow alarm faulting pump station . yes again . this is twice today | Type 3 | 2022-04-20 14:56:00 | 1
2021-2022 | INC-0055494 | Murray Bridge WWTP | Murray Bridge Lagoon WWTP (Govt Rd): Murray Bridge Effluent Reuse Wetland Outlet Pond B, SP4759: 31/03/22 Toxic BGA 832000 cells/mL Microcystis flos-aquae 2021-012-2559 31/03/22 4:59 am 420000 cells/mL Microcystis aeruginosa 2021-012-2559 31/03/22 4:59 am 412000 cells/mL | Type 1 | 2022-03-31 04:59:00 | 1
2021-2022 | INC-0055496 | Finger Point WWTP | Truck Driver was unloading chlorine drum of truck and was half way in building and snagged the electrical cable that drives the crane under the crane carriage coursing it to short out. The crane is run by a remote pendent and has no direct connection to the crane. It seems while the truck driver was unloading the Chlorine the wind was strong down there and may have swung the electrical cable around the drive carriage, this would not have been noticed by the Truck Driver as he would be focused on making sure he did not run into anything with the Chlorine drum. | Type 3 | 2022-05-04 09:00:00 | 1
2021-2022 | INC-0055535 | Millicent WWTP | Millicent Lagoon WWTP (Lossie Rd): SP4602 Lagoon 3 Effluent: Microcystis aeruginosa 9200 cells/mL | Type 2 | 2022-05-10 17:09:00 | 1
2021-2022 | INC-0055564 | Finger Point WWTP | Since December, sludge is coming into the WWTP inlet screen and is likely being formed due to the new configuration of the last 7kms of main (built in 2020). the screen is unable to process the sludge/waste material and it is causing overflowing of the screen and screw press and resulting in the screen being bypassed while the operators spend hours during the day washing the material through and manually processing. This is occurring daily, with the larger events being recorded in SAAM. This is consuming a significant amount of time for the operators and impacting on the basin. | Type 3 | 2022-05-13 09:00:00 | 1
2021-2022 | INC-0055588 | Port Lincoln WWTP | A very small power flick occurred causing Basin 1 timer reset to zero . this has cause a high basin level of 6.52 mtr. happened whilst in single basin operation | Type 3 | 2022-05-18 14:56:00 | 1
2021-2022 | INC-0055591 | Hahndorf Activated Sludge WWTP (Ambleside Rd) |  | Type 3 | 2022-05-09 08:00:00 | 1
2021-2022 | INC-0055605 | Naracoorte WWTP (Treatment Works Rd) | CCTV inspections undertaken for the outfall mains that runs from the treatment plant to the polishing lagoon off site before discharge. The mains carries secondary treated effluent which is not disinfected. The inspection identified multiple 2-5 mm circumferential cracks within the first 80 meters of the pipe. Multiple tree root intrusions were also identified. There is suspected effluent seepage into the environment through the cracks and also infiltration. | Type 3 | 2022-03-29 09:47:00 | 1
2021-2022 | INC-0055663 | Port Augusta West WWTP | Septic load was dumped outside bay, causing build up of material outside of the bond within the concrete pad. | Type 3 | 2022-05-23 09:00:00 | 1
2021-2022 | INC-0055733 | Finger Point WWTP | HiHi alarm float was not triggered due to sludge formation, operator performed check on screen and noticed build up. Wash water pump had also faulted and not spraying onto sludge to break it up. | Type 3 | 2022-06-02 11:35:00 | 1
2021-2022 | INC-0055751 | Port Augusta East WWTP | Site observations made by the Operator indicated the presence of water in a culvert between the road and WWTP boundary fence. Initial thoughts were the high ground water and recent rains over the decommissioned fly ash ponds (Port Augusta Power Station) was the source. Flow rate is < 1L/m with no obvious signs of higher flow. To confirm the source of the water sampling was conducted, this analysis has shown this water to have similar characteristics to sewer (alkalinity and ammonia) | Type 2 | 2022-06-03 10:51:00 | 1
2021-2022 | INC-0055801 | Finger Point WWTP | When operator arrived onsite, they noticed large amount of sludge built up in the screen and at 70%. The HiHi float alarm had not triggered as it was stuck upright in the sludge blanket. This meant that 'bypass' operation had not been triggered (closing of NV01) and could have eventually overflowed the screen. The plant operator also noticed that the bund sump pump was not working and the sump surrounding the screen was a foot deep in water. | Type 3 | 2022-06-04 22:00:00 | 1
2021-2022 | INC-0055812 | Finger Point WWTP | Pumps & pipework are unable to pump at sufficient instantaneous flow rate and overflows are unable to drain to wetland area due to previous project works to protect the washdown bore. Desludging contractors equipment was partially submerged. | Type 3 | 2022-06-04 22:30:00 | 1
2021-2022 | INC-0055819 | Finger Point WWTP |  | Type 3 | 2022-06-06 22:14:00 | 1
2021-2022 | INC-0055820 | Mount Burr WWTP | Rainfall over the weekend would have kept media wet and not resulted in die off, but would have caused poor treatment performance. Biofilter arm has rotation fault but oncall operator had not received a call. | Type 3 | 2022-06-07 08:27:00 | 1
2021-2022 | INC-0055877 | Port Lincoln WWTP | All four weirs faulted simultaneously. Weirs 1 and 2 faulted raised. Weirs 3 and 4 faulted down. | Type 3 | 2022-06-11 15:20:00 | 1
2021-2022 | INC-0055928 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Water line leaked in caustic chemical bund area floating liquid polymer bund and storage tank and capsizing tank (spilling contend) | Type 3 | 2022-06-19 17:00:00 | 1
2021-2022 | INC-0056015 | Port Lincoln WWTP | whilst cleaning grit receive station i opened the tractor door whilst traveling one wheel over mount Everest (over kill tyre stop) the tractor tilted and door hit grit receive hand railing and shattered . thankfully the windows/doors are tinted holding the all the glass together. | Type 3 | 2022-06-28 09:16:00 | 1
2021-2022 | INC-0056024 | Mannum WWTP | Mild summer weather conditions, golf course events and pump faults have resulted in lower levels of recycled water use this summer. Lagoon levels were not drawn down enough to manage capacity over winter. Levels currently very high - irrigation currently maintaining levels. Potential to cause damage to banks. | Type 3 | 2022-06-27 12:00:00 | 1
2021-2022 | INC-0056136 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): SP45813 Murray Bridge WWTP Effluent (Pre UV) Biochemical Oxygen Demand 2022-004-1270 17/06/22 4:59 am 40 mg/L | Type 3 | 2022-06-17 04:59:00 | 1
2022-2023 | INC-0056132 | Whyalla WWTP | All aerators in lagoon 1 & 2 Faulted for some reason. Call didn't come through until Monday morning. Tag help correct on lagoon 1 but not 2 | Type 3 | 2022-07-11 08:10:00 | 1
2022-2023 | INC-0056202 | Finger Point WWTP | Rag material causes low DO zone and causes aerators to run longer in the cycle. Over aeration can impact basin and settling, causing carry over of solids into polishing lagoons. High ammonia levels detected in polishing lagoons. Additional run time of aerators impacting on electricity usage and costs for plant. | Type 3 | 2022-07-15 14:00:00 | 1
2022-2023 | INC-0056244 | Christies Beach WWTP | Monday 18th July P&T notified FH Site Supervisor of a planned power outage which may result in potential effluent spill. The capacity of the C plant was managed and 3 stop logs were in place (Original, Temporary and 80% in works) but at approx. 1430hr the potential spill occurred from the Y channel into A Tank of PST. | Type 3 | 2022-07-18 14:30:00 | 1
2022-2023 | INC-0056247 | Millicent WWTP |  | Type 3 | 2022-07-20 09:00:00 | 1
2022-2023 | INC-0056277 | Finger Point WWTP |  | Type 3 | 2022-07-27 05:00:00 | 1
2022-2023 | INC-0056295 | Port Lincoln WWTP | Weir 4 faulted in low position 6.08m. | Type 3 | 2022-07-30 22:40:00 | 1
2022-2023 | INC-0056308 | Finger Point WWTP |  | Type 3 | 2022-07-31 21:00:00 | 1
2022-2023 | INC-0056309 | Finger Point WWTP | Operator called to site after both chlorine injector pumps had gone out on flow fail faults. | Type 3 | 2022-08-01 00:18:00 | 1
2022-2023 | INC-0056310 | Finger Point WWTP | Multiple motor oil faults have now occurred on this aerator and other aerators. The sensors detect oil flow on start up and shut down of aerators with time delay on each. Delay start time in program will need to be increased slightly to reduce nuisance faults. | Type 3 | 2022-07-30 12:20:00 | 1
2022-2023 | INC-0056312 | Port Augusta West WWTP | Operator detected high sludge level in Lagoon 3 impacting recycled water customer filter run times. | Type 3 | 2022-07-29 13:34:00 | 1
2022-2023 | INC-0056345 | Finger Point WWTP |  | Type 3 | 2022-08-03 09:00:00 | 1
2022-2023 | INC-0056366 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Clarifier #1 and A/C (Final) Effluent: High turbidity effluent to to high rainfall | Type 1 | 2022-08-05 00:00:00 | 1
2022-2023 | INC-0056367 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Loss of nitrification Investigating reason | Type 3 | 2022-08-04 00:00:00 | 1
2022-2023 | INC-0056379 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2022-2023 | INC-0056409 | Finger Point WWTP | The aerator cable has broken, leaving aerator 4 to move across against the aerator walkway. The plant operator was nearby at the time and pressed the emergency stop button to prevent further damage. Aerator cables are frequently breaking and RFEE has been submitted to Engineering for alternative solutions as rubber absorbers can no longer be soruced. | Type 3 | 2022-08-10 10:00:00 | 1
2022-2023 | INC-0056438 | Naracoorte WWTP (Treatment Works Rd) | Naracoorte experienced only around 15mm in 4hours on Friday night, but the collection area has been fully saturated. Additional flows came into the WWTP, with a high level peaking around 9pm, with plant operator needing to come to site for a high level alarm after the primary pumps had faulted and needed resetting. With all 4 pumps in the primary station and 2 pumps in the secondary station, capacity of the treatment plant was hydraulically exceeded and additional flows were sent to the salina partially/not treated. | Type 3 | 2022-08-12 21:00:00 | 1
2022-2023 | INC-0056468 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Lagoon#5 overflowing with Stormwater Due to recent rains etc, the levels in the old treatment Lagoons has increased with the inflows of stormwater | Type 3 | 2022-08-12 14:00:00 | 1
2022-2023 | INC-0056489 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Loss of PLC/SCADA control due to complications with system failure | Type 2 | 2022-08-16 16:00:00 | 1
2022-2023 | INC-0056508 | Finger Point WWTP | Rag material approximately 2 x 44gallon drums worth of material came in one clump into Finger Point screen blocking it and causing a high level. | Type 3 | 2022-08-22 12:00:00 | 1
2022-2023 | INC-0056636 | Finger Point WWTP |  | Type 3 | 2022-09-01 06:15:00 | 1
2022-2023 | INC-0056674 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Centrifuge not operational. Unable to waste. MLSS at 8000 mg/L (target 3000-5000) impacting aeration efficiency. Ammonia 8 mg/L (limit 1 mg/L) | Type 3 | 2022-09-05 09:00:00 | 1
2022-2023 | INC-0056733 | Port Lincoln WWTP |  | Type 3 | 2022-09-12 14:12:00 | 1
2022-2023 | INC-0056734 | Port Lincoln WWTP |  | Type 3 | 2022-09-12 14:15:00 | 1
2022-2023 | INC-0056735 | Port Lincoln WWTP | small cut in finger from knife whilst trying to cut rag from thickened was pumps | Type 3 | 2022-09-12 14:17:00 | 1
2022-2023 | INC-0056767 | Port Lincoln WWTP | Digester overflowed into Dewatering feed tank due to incorrect level sensor reading . | Type 3 | 2022-09-14 12:04:00 | 1
2022-2023 | INC-0056769 | Port Lincoln WWTP | Thunderstorm passed over causing a quick power flick resetting Aeration basin timers | Type 3 | 2022-09-14 14:52:00 | 1
2022-2023 | INC-0056870 | Port Lincoln WWTP | Power flick reset basin timers . requires operator intervention | Type 3 | 2022-09-28 14:07:00 | 1
2022-2023 | INC-0056911 | Port Lincoln WWTP | ALL 4 Weirs faulted causing both aeration basin to fault along with rest timers . happened twice approx 5 min apart | Type 3 | 2022-09-30 14:24:00 | 1
2022-2023 | INC-0056927 | Port Augusta West WWTP | Operator observed cracking within the bank of Lagoon 2 during routine vegetation clearing. Cracks were observed running in parallel to the lagoon water | Type 3 | 2022-09-30 12:30:00 | 1
2022-2023 | INC-0056933 | Port Lincoln WWTP | Both basins in storm cycle due to high incoming flows . long steady rain fall | Type 3 | 2022-10-04 12:36:00 | 1
2022-2023 | INC-0056970 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Hardstand Return Sump, foaming within wet well, most likely due to catchment of polymer laden (storm)water from hardstand runoff | Type 3 | 2022-10-06 10:59:00 | 1
2022-2023 | INC-0057015 | Normanville WWTP | On entering Normanville WWTP driving crane truck XQB660 on roadway leading down behind SBRs, back passenger tyre was punctured from a sharp corner of a metal retaining wall post. | Type 3 | 2022-10-13 07:30:00 | 1
2022-2023 | INC-0057025 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Low UV dose cause by high Suspended Solids in Effluent post disk filter | Type 1 | 2022-10-14 06:45:00 | 1
2022-2023 | INC-0057026 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Storms have caused the on site Lagoons to overflow through cutoff drain to Creek | Type 3 | 2022-10-14 09:11:00 | 1
2022-2023 | INC-0057076 | Port Augusta West WWTP | The RTU was shut down remotely at the plant at approx. 10:00 on the 14th. During a routine look onto SCADA, the whole plant was purple showing a no comms. A call to the OCC had it rectified quickly, and all comms came back online 16:00 on the 20th. The plant is operating ok, but we have no trending or history for the last | Type 3 | 2022-10-20 16:12:00 | 1
2022-2023 | INC-0057113 | Heathfield WWTP | The sludge holding area is flooded with rainwater causing the thickened sludge to become fluid and cover the complete area | Type 3 | 2022-10-18 08:47:00 | 1
2022-2023 | INC-0057129 | Port Augusta West WWTP | Recycled water system shutdown due to high residual (> 4.0mg/L) Dan Squire called to inform of high residual | Type 3 | 2022-10-27 01:00:00 | 1
2022-2023 | INC-0057132 | Murray Bridge WWTP (Brinkley) | SP45813: Murray Bridge WWTP Effluent (Pre UV): 125 mg/L | Type 3 | 2022-10-14 23:59:00 | 1
2022-2023 | INC-0057144 | Christies Beach WWTP | Issues with a turbidity meter was being investigated, whilst unit was in sim, grab samples tested and confirmed turbidity breakthrough on the train. Train was not shutdown in auto due to instrument being in sim mode during the fault-finding timeline. | Type 1 | 2022-10-28 13:38:00 | 1
2022-2023 | INC-0057158 | Heathfield WWTP | Solids carryover due to high inflows | Type 3 | 2022-11-01 12:14:00 | 1
2022-2023 | INC-0057159 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Solids carryover due to high inflows | Type 3 | 2022-11-01 12:17:00 | 1
2022-2023 | INC-0057160 | Whyalla WWTP | Operator reported erosion to the Northern bank of Lagoon 5. Likely due to wave action | Type 3 | 2022-11-01 09:00:00 | 1
2022-2023 | INC-0057161 | Whyalla WWTP | Operator identified milky appearance to the lagoon water, High solids levels within lagoon are noted. Lagoon is set for desludging in March '23 | Type 3 | 2022-11-01 09:00:00 | 1
2022-2023 | INC-0057187 | Whyalla WWTP | Operations detected high lagoon level in lagoons 4 and 5/6 during routine lagoon monitoring. There has been increased flow through the WWTP this year due to high rainfall combined with low evaporation rates across the Eyre Peninsula coupled with higher inflows | Type 3 | 2022-11-01 08:00:00 | 1
2022-2023 | INC-0057237 | Naracoorte WWTP (Treatment Works Rd) | High level alarm received for the Naracoorte WWTP Primary pump station wet well. Control room operator notificed that pump 4 was also out on fault. On call Operator called to site. | Type 3 | 2022-10-31 21:00:00 | 1
2022-2023 | INC-0057238 | Nangwarry WWTP | Imhoff tank overflowed to sludge lagoons. | Type 3 | 2022-10-21 17:00:00 | 1
2022-2023 | INC-0057259 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Ixom delivered a 'hot' order of alum to Hahndorf WWTP. Hot alum rendered instrumentation invalid | Type 3 | 2022-11-10 10:00:00 | 1
2022-2023 | INC-0057271 | Finger Point WWTP | Plant operator noticed that small patch of wet ground had not dried up on warm weather day like all of the other puddles around the plant. Dug down a bit and noticed soil surrounding was also wet. Leak also appeared to be intermittent. | Type 3 | 2022-11-08 09:00:00 | 1
2022-2023 | INC-0057319 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Final Effluent turbidity high due to Storm/High inflows | Type 3 | 2022-11-12 18:30:00 | 1
2022-2023 | INC-0057320 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Final Effluent turbidity high due to Storm/High inflows | Type 3 | 2022-11-14 05:50:00 | 1
2022-2023 | INC-0057323 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Final Effluent turbidity high due to Storm/High inflows | Type 3 | 2022-11-14 06:20:00 | 1
2022-2023 | INC-0057324 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): No Blower changeover for 6 hours No aeration for this time | Type 3 | 2022-11-12 06:30:00 | 1
2022-2023 | INC-0057325 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Loss of SCADA connection (Plant operations invisible for 1 hour) | Type 3 | 2022-11-12 16:30:00 | 1
2022-2023 | INC-0057326 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Loss of telephone comms | Type 3 | 2022-11-12 17:30:00 | 1
2022-2023 | INC-0057327 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Loss of power changeover switch (Generator, UPS systems) UPS systems would not recharge without changeover switch in operation ... if generator is running, runs Admin building, UPS system and UV disinfection | Type 3 | 2022-11-12 16:10:00 | 1
2022-2023 | INC-0057424 | Port Lincoln WWTP |  | Type 3 | 2022-11-19 10:20:00 | 1
2022-2023 | INC-0057425 | Port Lincoln WWTP | Operator Attended Site | Type 3 | 2022-11-20 00:35:00 | 1
2022-2023 | INC-0057426 | Port Lincoln WWTP |  | Type 3 | 2022-11-20 09:20:00 | 1
2022-2023 | INC-0057427 | Port Lincoln WWTP |  | Type 3 | 2022-11-21 03:30:00 | 1
2022-2023 | INC-0057428 | Port Lincoln WWTP |  | Type 3 | 2022-11-21 10:45:00 | 1
2022-2023 | INC-0057457 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Operator noticed during routine monitoring that the leg of the surface aerator in Sludge Lagoon 2 was broken. Operator proceeded to turn aerator off and notify supervisor of the breakage. | Type 3 | 2022-11-01 10:30:00 | 1
2022-2023 | INC-0057463 | Normanville WWTP | Loss of disinfection due to PLC issues involved in cutover process | Type 1 | 2022-11-25 07:00:00 | 1
2022-2023 | INC-0057475 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV disinfection and A/UV Effluent: Process failure causing decrease in A/UV Effluent below validation limits of UV disinfection equipment | Type 1 | 2022-11-28 10:00:00 | 1
2022-2023 | INC-0057508 | Port Lincoln WWTP | No 1 aeration basin was taken offline and lowered level for an Engineering inspection of the decant structure. When the basin was lowed, the floating aerators dropped lower than expected and damaged electrical plugs. | Type 3 | 2022-11-30 15:57:00 | 1
2022-2023 | INC-0057509 | Christies Beach WWTP | Train 1 returned to service after a clean cycle, NTU was greater than 0.2 on start-up, NTU settled down and settled below 0.2 NTU. SCADA DOH page indicated no breach in 24 hour average 0.13NTU (see attachment), ODS daily report did indicated a a breach of 0.23 NTU | Type 2 | 2022-11-30 16:30:00 | 1
2022-2023 | INC-0057587 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Ditch #2: Aerator failure: Rotors 2A and 2B: Aeration failure resulted in high suspended solids effluent being discharged to Hahndorf Creek | Type 1 | 2022-12-08 11:00:00 | 1
2022-2023 | INC-0057620 | Port Lincoln WWTP | Both dewatering train hoppers blocked with cake causing overflow into dewatering building floor | Type 3 | 2022-12-12 11:47:00 | 1
2022-2023 | INC-0057661 | Naracoorte WWTP (Treatment Works Rd) | Copper pipework has been replaced multiple times in recent years, but will now be replaced with more expensive stainless steel in the hope that it will last longer and reduce call outs by a plumber. Leaks occurring in primary and secondary rooms, cause water on the floor of the pump station which is a safety hazard and requires to be pumped out. Unfortunately, site is still not metered, so difficult to determine how much water is constantly being lost due to water leaks from site. Request has been with field ops team for > 12months. Contractor to be organised in near future to tackle mounting backlog list of works. | Type 3 | 2022-12-16 07:20:00 | 1
2022-2023 | INC-0057665 | Mannum WWTP | Small land slide behind imhoff tank compound, security fence stopped spoil from entering the imhoff compound | Type 3 | 2022-12-16 11:35:00 | 1
2022-2023 | INC-0057674 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | On leaving Bird In Hand WWTP noticed that passenger side toolbox door had flung open, & on investigation found that a bolt holding the door latch closed had broken. | Type 3 | 2022-12-16 14:09:00 | 1
2022-2023 | INC-0057697 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3 hours | Type 3 | 2022-12-16 12:30:00 | 1
2022-2023 | INC-0057698 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3 hours | Type 3 | 2022-12-17 14:50:00 | 1
2022-2023 | INC-0057699 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 5 hours | Type 3 | 2022-12-22 16:00:00 | 1
2022-2023 | INC-0057700 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Black Sewage inflow into Plant | Type 3 | 2022-12-22 11:00:00 | 1
2022-2023 | INC-0057701 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): Low UVT Influent into Plant: Affecting UV system | Type 3 | 2022-12-22 17:00:00 | 1
2022-2023 | INC-0057714 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 5 hours | Type 3 | 2022-12-23 12:00:00 | 1
2022-2023 | INC-0057719 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Apparent chlorine interruption | Type 3 | 2022-12-27 23:00:00 | 1
2022-2023 | INC-0057739 | Finger Point WWTP | Finger Point screen is inadequate. Multiple capital projects raised to deal with the issue but solution has not yet been delivered. Plant Operators required to manual handle rag material up screen, resulting in excessive time being spent on its operation and not on other plant activities. This is a strain with a very small group of operators across a large number of plants and well being is being impacted from old, broken and undersized infrastructure. | Type 3 | 2022-12-30 16:10:00 | 1
2022-2023 | INC-0057774 | Port Augusta East WWTP | Port Augusta East sewage (SP4721) has been unavailable for sampling since redesign and construction of the inlet chamber (replaced with pipework for flow split). The autosampler is unable to draw sample through the sampling point due to high draw length and low back pressure on the main. | Type 3 | 2023-01-04 08:27:00 | 1
2022-2023 | INC-0057779 | Murray Bridge WWTP (Brinkley) | Anomaly in operation of dewater system in plant PLC , SCADA system graphics not matching plant in field , pumps operating when they should be stopped. Plant not operating in auto when not in fault and all systems appear available | Type 3 | 2023-01-03 11:50:00 | 1
2022-2023 | INC-0057783 | Normanville WWTP | Normanville WWTP: Activated Sludge Plant Process operating suboptimally | Type 1 | 2023-01-04 15:36:00 | 1
2022-2023 | INC-0057887 | Port Lincoln WWTP | Horse hair algae collected on the screen causing high turbidity from the raw water pumps. Operators attempted to clear, ongoing works being conducted to clear screen | Type 1 | 2023-01-11 13:00:00 | 1
2022-2023 | INC-0057918 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2022-2023 | INC-0057933 | Finger Point WWTP | Material pushed up and over the top of screw press was approx 3 wheelbarrows worth of material causing some damage to the top of the screen. There was also material blocking the step screen and material all the way back past NV01 Inlet valve. | Type 2 | 2023-01-16 11:39:00 | 1
2022-2023 | INC-0057958 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3 hours | Type 3 | 2023-01-14 04:15:00 | 1
2022-2023 | INC-0057959 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3.5 hours | Type 3 | 2023-01-15 15:15:00 | 1
2022-2023 | INC-0057960 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 13 hours | Type 3 | 2023-01-17 13:00:00 | 1
2022-2023 | INC-0057964 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 4.75 hours | Type 3 | 2022-12-24 12:15:00 | 1
2022-2023 | INC-0057968 | Mount Burr WWTP | Pumps supplying flow over biofilter have dropped in efficiency and creating a biofilter rotation fault as it periodically stops rotating. | Type 3 | 2023-01-18 10:02:00 | 1
2022-2023 | INC-0057969 | Finger Point WWTP | Power flick during decanting has stopped the process | Type 3 | 2023-01-17 16:00:00 | 1
2022-2023 | INC-0057970 | Finger Point WWTP | Plant operator notified of a power outage at Finger Point. Est time to restore water 5hours. | Type 3 | 2023-01-18 16:00:00 | 1
2022-2023 | INC-0057974 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 15 hours | Type 3 | 2023-01-18 11:00:00 | 1
2022-2023 | INC-0058018 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 11 hours | Type 3 | 2023-01-19 15:00:00 | 1
2022-2023 | INC-0058019 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 11 hours | Type 3 | 2023-01-21 18:00:00 | 1
2022-2023 | INC-0058046 | Whyalla WWTP | Routine observations of Whyalla WWTP showed one aerator in lagoon 2 is tilted indicating the float is compromised. | Type 3 | 2023-01-24 10:00:00 | 1
2022-2023 | INC-0058057 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3 hours | Type 3 | 2023-01-25 11:45:00 | 1
2022-2023 | INC-0058059 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 7.75 hours | Type 3 | 2023-01-26 15:00:00 | 1
2022-2023 | INC-0058091 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 14.5 hours | Type 3 | 2023-01-27 12:00:00 | 1
2022-2023 | INC-0058093 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 14 hours | Type 3 | 2023-01-28 12:45:00 | 1
2022-2023 | INC-0058095 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Power outage/flick likely to have been result of a pelican touching the power lines as a grass fire was reported shortly after alarm call in vicinity of Cape Jaffa. | Type 3 | 2023-01-27 21:30:00 | 1
2022-2023 | INC-0058202 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 2.75 hours | Type 3 | 2023-02-01 11:45:00 | 1
2022-2023 | INC-0058204 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 7 hours | Type 3 | 2023-02-01 20:00:00 | 1
2022-2023 | INC-0058251 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3.25 hours | Type 3 | 2023-02-02 13:45:00 | 1
2022-2023 | INC-0058252 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity (total of) 25 hours (... in three stages) | Type 3 | 2023-02-03 01:00:00 | 1
2022-2023 | INC-0058253 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 9.5 hours | Type 3 | 2023-02-04 14:30:00 | 1
2022-2023 | INC-0058254 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity 3.25 hours | Type 3 | 2023-02-06 13:45:00 | 1
2022-2023 | INC-0058257 | Nangwarry WWTP | High water level was real as operator had found water laying in sludge lagoon. | Type 3 | 2023-02-05 11:09:00 | 1
2022-2023 | INC-0058269 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Effluent After UV SP42969: E.coli 54 MPN/100mL | Type 3 | 2023-02-03 04:59:00 | 1
2022-2023 | INC-0058270 | Whyalla WWTP | TARP WWTP h2s odour sensor spike, lagoon 3 | Type 3 | 2023-02-08 08:10:00 | 1
2022-2023 | INC-0058272 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): AC Effluent SP4555: High ammonia and SS | Type 3 | 2023-02-08 08:23:00 | 1
2022-2023 | INC-0058281 | Myponga WWTP | Myponga Lagoon WWTP (James Trac): Irrigation Effluent SP4592: Microcystis flos-aquae 11700 cells/mL | Type 2 | 2023-01-19 04:59:00 | 1
2022-2023 | INC-0058285 | Murray Bridge WWTP (Brinkley) | Operations identified the pressure of the recycled water main decreased below normal operating pressure (>300kPa). Flow rate increased to 32L/s and pressure was sustained at 160 to 175 kPa until the pumps were turned off. | Type 1 | 2023-02-08 15:40:00 | 1
2022-2023 | INC-0058286 | Bird In Hand WWTP | Wiring in the chemical delivery area has been damaged by rodents. An electrician will need to be on site to activate the breaker behind the board to enable chemical deliveries. New cable is onsite needs to be installed. | Type 2 | 2023-02-08 15:51:00 | 1
2022-2023 | INC-0058342 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity (total of) 10 hours (... in two stages) | Type 3 | 2023-02-13 10:00:00 | 1
2022-2023 | INC-0058343 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine Contact Tank High Turbidity (total of) 14ours (... in three stages) | Type 3 | 2023-02-14 07:00:00 | 1
2022-2023 | INC-0058345 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2022-2023 | INC-0058372 | Murray Bridge WWTP | Murray Bridge Effluent Reuse Wetland Outlet Pond B, SP4759: 31/01/23 10:00 am 19400 cells/mL (Microcystis aeruginosa 14400 cells/mL, Microcystis flos-aquae 5000 cells/mL) | Type 1 | 2023-01-31 10:00:00 | 1
2022-2023 | INC-0058412 | Normanville WWTP | Normanville WWTP: Links Lady Bay Storage SP90159: E.coli 1600 MPN/100mL (non-representative sample) | Type 3 | 2023-02-16 04:59:00 | 1
2022-2023 | INC-0058418 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): High BOD 07/02/2023 52 mg/L | Type 3 | 2023-02-07 00:00:00 | 1
2022-2023 | INC-0058424 | Glenelg Waste Water Treatment Plant |  | Priority Type 1 | 2023-02-23 02:25:00 | 1
2022-2023 | INC-0058427 | Glenelg Waste Water Treatment Plant | Chlorination PLC failed which caused GARWS to shutdown automatically. | Type 2 | 2023-02-23 01:05:00 | 1
2022-2023 | INC-0058466 | Finger Point WWTP | Finger Point WWTP Outflow Weir: SP4879: E.coli 2 MPN/100mL | Type 3 | 2023-02-23 04:59:00 | 1
2022-2023 | INC-0058498 | Port Lincoln WWTP |  | Type 3 | 2023-03-01 08:30:00 | 1
2022-2023 | INC-0058513 | Port Lincoln WWTP | Operator was informed by OCC that no biogas burner was available. The operator attempted a manual reset of the burner which worked, however the fault reoccured within 15 minutes. The operator attempted the reset several times however the fault remained. | Type 3 | 2023-02-09 12:00:00 | 1
2022-2023 | INC-0058541 | Mannum WWTP | Sample from lagoon 2 taken on 3.3.23 showed 3400 MPN/100ml. | Type 3 | 2023-03-04 10:30:00 | 1
2022-2023 | INC-0058607 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Numerous simultaneous Process instabilities: High Effluent nitrate: Low inflow carbon load High Effluent phosphate: Issues with alum dosing system No Reuse water for flushing, cleaning, dosing etc due to pipework failure | Type 3 | 2023-03-10 13:59:00 | 1
2022-2023 | INC-0058708 | Whyalla WWTP | Customer reported high odour around the caravan park with several reports from guests about the odour | Type 3 | 2023-03-19 08:04:00 | 1
2022-2023 | INC-0058723 | Port Lincoln WWTP | Reuse chlorine booster pump faulted on NO flow shutting down reuse plant. interrupting Councils water supply. Found Filter to be partially blocked and flow meter probe dirty. | Type 2 | 2023-03-20 07:55:00 | 1
2022-2023 | INC-0058724 | Port Lincoln WWTP | Reuse plant, raw feed VSD Faulted (mains failure), caused plant to shut down. tank pumped down then council supply was interrupted | Type 2 | 2023-03-21 08:03:00 | 1
2022-2023 | INC-0058776 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-03-21 09:30:00 | 1
2022-2023 | INC-0058803 | Port Lincoln WWTP | All 4 Weirs faulted. causing both Aeration basins to fault and timers to reset. operator intervention is required. | Type 3 | 2023-03-28 15:15:00 | 1
2022-2023 | INC-0058812 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Cape Jaffa WWTP does not have an inlet screen so material can pass through system. | Type 3 | 2023-03-28 09:11:00 | 1
2022-2023 | INC-0058891 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Back on the 16th of September 2022 Disc Filters A & B at the Bird In Hand WWTP have not been running & are being bypassed due to the electrical components being flooded from power issues. Operators are having to clean filters daily, reset faults & is effecting the effluent quality. | Type 3 | 2023-04-06 06:59:00 | 1
2022-2023 | INC-0058892 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | The Chemical Storage & Dosing area at Bird In Hand WWTP had rats damage the electrical cables to the caustic components of the plant back on the 28th of June 2022. This affected not only the caustic dose pumps, but also the sump pump, loading power supply, security beacon & Operators routine checks. New cables were relayed last year, but may need to be relayed again due to not having been connected & weather damage to cable ends. | Type 3 | 2023-04-06 07:36:00 | 1
2022-2023 | INC-0058896 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | General alarms received at 2:36pm and 6:50pm. Weather may have impacted supply. | Type 3 | 2023-04-06 19:00:00 | 1
2022-2023 | INC-0058926 | Myponga Beach WWTP | Myponga Beach WWTP Irrigation Supply: E.coli 16000 MPN/100mL | Type 1 | 2023-04-12 12:15:00 | 1
2022-2023 | INC-0059005 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): Final Effluent (Post UV) SP45812 E.coli 200/100mL and Effluent (Pre UV) SP45813 BOD 67 mg/L | Type 3 | 2023-04-12 12:30:00 | 1
2022-2023 | INC-0059007 | Wirrina Cove WWTP | Wirrina Cove WWTP: Tank 3 (Final Effluent) SP93749: BOD 82 mg/L, BODsol 48 mg/L | Type 3 | 2023-04-11 11:28:00 | 1
2022-2023 | INC-0059021 | Nangwarry WWTP | Alerted to Nangwarry WWTP after High level alarm in Imhoff tank and found that imhoff tank had overflowed to sludge lagoon. | Type 3 | 2023-04-17 09:17:00 | 1
2022-2023 | INC-0059023 | Murray Bridge WWTP (Brinkley) | The Disk filters at the Murray Bridge Brinkley WWTP are used to remove solids from the MBBR treatment process after the (Lamella) Clarifiers ... one Filter set (Filter #2) was already inoperable (and out of operation for repairs), and the remaining operational and on line Disk filter (Filter #1) was removed from the process | Type 3 | 2023-04-20 09:00:00 | 1
2022-2023 | INC-0059029 | Finger Point WWTP | Pump1 was out on No flow and overload fault, Pump 2 was out on flow fault. | Type 3 | 2023-04-20 06:15:00 | 1
2022-2023 | INC-0059043 | Port Lincoln WWTP | Water Heater 1 became unavailable due to fouling. Water Heater 2 unavailable - awaiting new temperature probe to be installed System operates with a Duty Duty water Heater setup. Water Heater 2 was serviced 10/2/23 and has been utilised exclusively since servicing. Water Heater 1 has been out of service since 2/12/23 | Type 3 | 2023-04-23 13:10:00 | 1
2022-2023 | INC-0059069 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | No previous notification for outage from SAPN has occurred. Estimated outage was approximately 4hours. Indications are that power to the site is being split and a separate meter connections are being installed for WWTP and Quarry. | Type 2 | 2023-04-26 09:35:00 | 1
2022-2023 | INC-0059072 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Site was restored at 4:26am. Unknown how long outage was for. Water supply and Wastewater treatment plant were out, unknown whether networks was impacted. | Type 3 | 2023-04-22 04:26:00 | 1
2022-2023 | INC-0059076 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Emergency E stop alarm received which is usually indicative of a power outage. Storm rolled through district about the same time. Water Supply tank >80%. | Type 3 | 2023-04-27 06:20:00 | 1
2022-2023 | INC-0059078 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | SAPN early ETA for restoration time is 3pm. Plant Operator was on route to site as unable to reset alarms from previous outage earlier this morning. UPS battery life was poor. | Type 3 | 2023-04-27 08:45:00 | 1
2022-2023 | INC-0059082 | Christies Beach WWTP | The turbidity started to rise after train 3 was put back online after a maintenance wash. The turbidity was higher than normal between 2.02pm and 2.45pm on the 26/4/23. | Type 2 | 2023-04-27 12:31:00 | 1
2022-2023 | INC-0059098 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | SAPN Outage | Type 3 | 2023-04-28 06:30:00 | 1
2022-2023 | INC-0059099 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-04-28 08:50:00 | 1
2022-2023 | INC-0059105 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-04-29 21:30:00 | 1
2022-2023 | INC-0059160 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2022-2023 | INC-0059178 | Heathfield WWTP | Current condition of Digested sludge, and operation of Centrifuge has caused inefficient dewatering | Type 3 | 2023-05-04 11:13:00 | 1
2022-2023 | INC-0059184 | Wirrina Cove WWTP | Wirrina Cove WWTP: Aerator Failure in (Constant) Aeration Tank | Type 3 | 2023-05-04 14:35:00 | 1
2022-2023 | INC-0059189 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Level sensor in SBR tank causing faults. Interference from aerators and general windy conditions on site causing multiple alarms (12) coming through at 1:48, 2:36, 3:50 and 10:40. | Type 3 | 2023-05-03 01:50:00 | 1
2022-2023 | INC-0059244 | Port Augusta West WWTP | Workshops teams were alerted to a system fault at Port Augusta West WWTP at 0300 on 07/5/23, crews attended and ensured chlorine drums were interlocked and no leaks/residual on external indicator. Electricians were dispatched Monday morning and found the UPS system which supplied backup power to HydraSentinal system had faulted as the power supply to the UPS had tripped a fuse not accessible by Operator. Treated effluent was discharged to the Environment (Lake Dempsey) from 1400 07/05/23 until 1600 08/05/23 at 5.5 L/s, the system has been reset and golf course flow is expected to run at 2000hrs 08/05/23 | Type 3 | 2023-05-08 08:30:00 | 1
2022-2023 | INC-0059253 | Nangwarry WWTP | An unknown and regular event is causing a high level in the imhoff tank at Nangwarry WWTP, with overflows being captured by the sludge lagoon. The events are short in duration and have subsided by the time an operator attends site (>1-2 hour attendance to site). | Type 3 | 2023-05-09 12:15:00 | 1
2022-2023 | INC-0059255 | Whyalla WWTP | Aerators in lagoon 1 made unavailable due to desludging activities in Whyalla Lagoon 1. Required to be turned off to minimise contamination potential of contractors performing desludge activities. Potential loss of process performance due to reduced aeration. | Type 3 | 2023-05-01 15:54:00 | 1
2022-2023 | INC-0059313 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | This afternoon (around 3pm) MDJV site representative noticed that effluent (more than 5L) was overflowing out of the second holding tank into the in-situ bund built around the tanks. Immediately reported the situation to the Waternish Supervisor, who then investigated, and noticed that the value to the first holding tank was closed. He then opened the value to balance the tanks and stop the overflow. | Type 3 | 2023-05-17 15:00:00 | 1
2022-2023 | INC-0059349 | Christies Beach WWTP | Turbidity for Train 5 appears to gradually increase, starting from 8am 20/05/2023, however the values remain within acceptable operating range until ~7pm 20/05. The daily average turbidity for 20/5 is taken at 12pm and includes the previous days good results, appearing normal at 0.06NTU. As the turbidity continued to increase overnight to 0.4, the daily average turbidity increased over 0.2NTU. Operator received high daily average alarm on 21/05 at 12pm when the calculation for the day is completed, with a daily average of 0.26NTU and shutdown the train; it had been running for 13.1 hours. Train 5 is at end of life and due to be replaced in coming weeks. | Type 2 | 2023-05-21 12:00:00 | 1
2022-2023 | INC-0059395 | Port Lincoln WWTP | whilst on return travel from Whyalla on the Lincoln hwy , an emu ran out onto the road and hit the side of the ute. i managed to swerve and brake reducing the severity leaving a minor dent in left rear door. unfortunately after impact the emu was still alive with a broken leg and needed to be put down. during this Marty Eling fell to the ground and rolled into the scrub causing minor scratches to his right elbow (scratches not requiring any attention). | Type 3 | 2023-05-25 09:00:00 | 1
2022-2023 | INC-0059408 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-05-26 18:25:00 | 1
2022-2023 | INC-0059412 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Final Effluent A/C turbidity > 10 NTU and effluent is released to receiving waters for > 2 continual hours | Type 2 | 2023-05-28 11:10:00 | 1
2022-2023 | INC-0059443 | Angaston WWTP | Operator reported finding 23 deceased ducks on the lagoon banks at Angaston WWTP. Operator reported similar occurrence last year at a similar time. May be related to post growth season spraying occurring in the vineyards adjacent to the WWTP. | Type 3 | 2023-05-26 10:19:00 | 1
2022-2023 | INC-0059444 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | There was a hydraulic oil spill (approx. 5-10L) at approximately 4:45pm at the TFI WWTP site. The final load of cement treated rubble was being tipped off, when it was noticed that the hydraulic line had a leak, spraying out onto the truck and freshly laid cement treated material. | Type 3 | 2023-05-31 07:55:00 | 1
2022-2023 | INC-0059447 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): Effluent (Pre UV) SP45813: BOD 26 mg/L, SS 35 mg/L, E.coli 48 MPN/100mL | Type 3 | 2023-05-22 12:00:00 | 1
2022-2023 | INC-0059469 | Port Lincoln WWTP | Power flicked at site causing multiple alarms and faults. | Type 3 | 2023-06-02 22:50:00 | 1
2022-2023 | INC-0059507 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): Clarifiers: Higher than normal turbidity | Type 3 | 2023-06-07 15:36:00 | 1
2022-2023 | INC-0059518 | Finger Point WWTP |  | Type 3 | 2023-06-07 16:00:00 | 1
2022-2023 | INC-0059519 | Nangwarry WWTP |  | Type 3 | 2023-06-07 20:00:00 | 1
2022-2023 | INC-0059520 | Finger Point WWTP |  | Type 3 | 2023-06-07 20:00:00 | 1
2022-2023 | INC-0059524 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Final Effluent A/C Turbidity >10 NTU, >2 hours (Total 4.5 hours) | Type 2 | 2023-06-08 22:40:00 | 1
2022-2023 | INC-0059564 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): A/C Effluent ex CCT Turbidity >10 NTU for 3 hours (19:40pm to 10:40pm) | Type 2 | 2023-06-13 19:40:00 | 1
2022-2023 | INC-0059566 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Effluent after UV SP42768 Ammonia 6.673 mg/L | Type 3 | 2023-05-30 04:59:00 | 1
2022-2023 | INC-0059582 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | VSD card failure in Sludge thickening area due to local power failure. Last spare card used to replace failed card no further spare cards available. Plant is now in danger of not being able to function correctly if another card is lost. | Type 3 | 2023-06-14 15:07:00 | 1
2022-2023 | INC-0059583 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2022-2023 | INC-0059584 | Naracoorte WWTP (Treatment Works Rd) | Contractor engaged by Security team to undertake security audit for capital works occurring in the next 12month period. Undertaking inspections only at this stage, so lower risk. Blue card inductions performed, but no site inductions and not escorted. General familiarisation with SAW sites. | Type 3 | 2023-06-15 13:22:00 | 1
2022-2023 | INC-0059639 | Port Lincoln WWTP | rain event has cause basin 1 to go into storm cycle | Type 3 | 2023-06-21 09:59:00 | 1
2022-2023 | INC-0059641 | Port Lincoln WWTP | Rain event has cause Basin 2 to go into a storm cycle . Both basin are now in a storm cycle . potential for water quality issues Basin went into storm cycle in 2 consecutive cycles | Type 3 | 2023-06-21 10:20:00 | 1
2022-2023 | INC-0059644 | Port Lincoln WWTP | Rain event has caused high inflows, causing both aeration basin into storm cycle . and now causing a high water level in basin 2 . potential for water quality issues. | Type 3 | 2023-06-21 10:33:00 | 1
2022-2023 | INC-0059664 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2023-06-01 08:00:00 | 1
2022-2023 | INC-0059674 | Port Lincoln WWTP | Both Aeration basins in storm cycle causing basin 2 to reach high level alarm. potential water quality issues. | Type 3 | 2023-06-23 10:39:00 | 1
2022-2023 | INC-0059676 | Heathfield WWTP | Inflow to plant in excess of 120 litres per second due to storm event. High inflows interrupt the treatment process leading the carryover of solids in final effluent. | Type 3 | 2023-06-23 12:47:00 | 1
2022-2023 | INC-0059678 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Storm event, high inflows lead to some carry over of solids in the final effluent. | Type 3 | 2023-06-23 12:53:00 | 1
2022-2023 | INC-0059679 | Gumeracha WWTP | Storm event, Inflow rate greater than outflow rate leading to an elevated level in Final Lagoon. Potential overflow of lagoon. | Type 3 | 2023-06-23 12:58:00 | 1
2022-2023 | INC-0059684 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High Outlet Turbidity due to Storm inflows | Type 2 | 2023-06-22 14:30:00 | 1
2022-2023 | INC-0059685 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): High turbidity outflows due to storm event | Type 2 | 2023-06-22 13:30:00 | 1
2022-2023 | INC-0059721 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-06-27 07:15:00 | 1
2022-2023 | INC-0059722 | Nangwarry WWTP | Regular high flows being experienced in this catchment requiring further investigation. Cause in this instance likely due to heavy period of rainfall. | Type 3 | 2023-06-25 09:00:00 | 1
2022-2023 | INC-0059732 | Point Pearce WWTP (Parrys Av) | OCC called to inform that the aeration tank had hit High level (95%). Tank appears to not have decanted since manually decanted by Dan/Nathan today at 10am | Type 3 | 2023-06-28 18:21:00 | 1
2022-2023 | INC-0059733 | Point Pearce WWTP (Parrys Av) | The aeration tank had hit High level (103%). Tank appears to not have decanted since manually since previous days attendance by Council | Type 3 | 2023-06-28 11:24:00 | 1
2022-2023 | INC-0059741 | Port Augusta East WWTP | Crew working to excavate area struck comms cable | Type 3 | 2023-06-26 10:00:00 | 1
2022-2023 | INC-0059919 | Murray Bridge WWTP (Brinkley) | After a Blower fault, the process at Murray Bridge Brinkley WWTP suffered and produced effluent lower than the validated transmissivity validation for the UV disinfection equipment | Type 3 | 2023-06-07 13:45:00 | 1
2022-2023 | INC-0064206 | Port Augusta West WWTP | Lagoon 1 receives sewage from Port Augusta West township and is an aerated lagoon. The flow is then going directly from Lagoon 1 into Lagoon 3 for polishing prior to reuse. The lagoon bank has longitudinal cracks along the entire length of the lagoon bank and has sunk down on the Lagoon 3 side of the bank. A truck was designed to be able to drive a truck along the bank and it is now only accessible by foot. The pole which was used as an anchor point to tie an aerator to used to be vertical and is now on a 45 degree angle. | Type 2 | 2022-11-01 12:00:00 | 1
2023-2024 | INC-0059863 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): High Outflow turbidity 08/07/2023 multiple events (10 hours out of 16 hours) | Type 2 | 2023-07-08 10:15:00 | 1
2023-2024 | INC-0059868 | Millicent WWTP |  | Type 3 | 2023-07-10 08:49:00 | 1
2023-2024 | INC-0059887 | Naracoorte WWTP (Treatment Works Rd) | Grit chamber was pumped out less than a week ago. Mains into the plant are gravity and high flows over the weekend likely to have scoured the inside of pipes, bringing in large quantities of material into the WWTP. Grit chamber is after the screen, so material will likely settle throughout plant. Potential for biofilter to become clogged up with material. | Type 3 | 2023-07-11 08:00:00 | 1
2023-2024 | INC-0059935 | Murray Bridge WWTP (Brinkley) | At approximately 06:00am on 16/07/2023 the Murray Bridge Brinkley WWTP Blowers inhibited. I believe that they tried to restart as per PLC, failed again and remained inhibited. This didn't initiate a callout from the system, and the process subsequently deteriorated over the preceding hours. The On call Operator was called out at approximately 17:30pm with a low UV transmissivity alarm and attended site. The Operator then reinitiated Blower operations and diverted outflow from the supply to the Army Range to the on site Swale to as to not put out of specification effluent into the system for the >60 minute designation via WWINC Operator attended site approximately 18:20pm. | Type 3 | 2023-07-16 18:20:00 | 1
2023-2024 | INC-0060015 | Mannum WWTP | Small pool of water was identified outside lagoon 2 bank in the excavated area being remediate by contractor. | Type 3 | 2023-07-21 11:00:00 | 1
2023-2024 | INC-0060135 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-08-03 03:45:00 | 1
2023-2024 | INC-0060144 | Heathfield WWTP | Heathfield WWTP Clarifier 3 carryover, Due to earlier rain even and high solids in the reactor. turbidity has been above 10 NTU since 11:31am currently turbidity after UV 2.60 Chlorine contact Tank turbidity is 14.49 | Type 2 | 2023-08-04 16:10:00 | 1
2023-2024 | INC-0060225 | Victor Harbor (Boot) WWTP | Incident: • Fire in Membrane Tank Blower #1 Results/Outcomes: • No injuries • Fire contained to Blower #1, no impact to any surrounding equipment, infrastructure, or environment. • Site Operations were not affected by the incident. Timeline of events: 15th August 2023 • 15:51 On Call Process Controller (PC) received a call from SCADA noting Blower 1 drive fault. • 15:52 PC logged into SCADA system remotely to investigate. Drive would not reset remotely so PC immediately returned to site. • 16:01 PC arrived at site and noticed black smoke coming from Blower 1 cabinet. o PC sourced nearby 9kg chemical fire extinguisher and attempted to extinguish the fire. Extinguisher emptied and fire partially extinguished. o PC headed to switch room and isolated Blower#1 main circuit breaker to cut power from the area. o PC returned to Blower #1 and used a high-pressure water hose to completely extinguish the fire. • 16:05 PC called second PC to return to site to assist and continued to cool hot metal parts. • 16:17 PC notified Operations Manager, who notified Regional Manager. • 17:56 PC’s ensured site was safe but untouched, captured critical details and left site. | Type 2 | 2023-08-16 09:15:00 | 1
2023-2024 | INC-0060232 | Point Pearce WWTP (Parrys Av) | Transfer pump did not run as expected to transfer decanted effluent from WWTP to RWTP, this caused the decant tank to fill over the overflow point causing discharge to the fenced bamboo overflow area. | Type 2 | 2023-08-17 09:00:00 | 1
2023-2024 | INC-0060241 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-08-17 15:30:00 | 1
2023-2024 | INC-0060285 | Port Lincoln WWTP | all 4 weirs faulted, putting both aeration basins into fault. basin 1 would have gone into storm cycle | Type 3 | 2023-08-24 19:30:00 | 1
2023-2024 | INC-0060291 | Wirrina Cove WWTP | Wirrina Cove WWTP: Poor quality effluent from Decant Tank | Type 3 | 2023-08-25 13:35:00 | 1
2023-2024 | INC-0060300 | Port Augusta East WWTP | During desludging works at the Port Augusta East WWTP the contractor hit the outfall main with the dredge auger. The contractor noticed a reduction in water level after lunch, contractor called local operator who attended site at 16:30 and assessed situation. Reported that water level had decreased in lagoon 4 by 400 - 500mm. This was confirmed by TPO via SCADA which showed flowrate leaving WWTP increased from 10-25 L/s to 77 to 81 L/s at 10:30am August 25th. | Type 2 | 2023-08-25 16:50:00 | 1
2023-2024 | INC-0060306 | Port Lincoln WWTP | All 4 weirs faulted causing both aeration basins to go into fault. this has happened 3 times on this day. weirs on basin 2 always seem to be in operation at the time. end ed up running plant in single basin operation on basin 1 | Type 3 | 2023-08-27 13:00:00 | 1
2023-2024 | INC-0060309 | Port Lincoln WWTP | Started getting a number of Reuse RTU faults again for the reuse plant today . | Type 3 | 2023-08-28 10:49:00 | 1
2023-2024 | INC-0060345 | Port Lincoln WWTP | small power flick caused basins to fault resetting timers . flick was so small the computer didn't even turn off | Type 3 | 2023-08-29 15:55:00 | 1
2023-2024 | INC-0060374 | Port Lincoln WWTP | carry water fault occurred which did not shutdown dewatering. RSP1 and sludge pump continued to run. | Type 3 | 2023-09-05 10:20:00 | 1
2023-2024 | INC-0060379 | Port Lincoln WWTP | Dewatering carry water low fault did not fault RSP 1 . resulting in digested sludge in RSP and outloading bays . sludge pump and RSP seem to continue to run | Type 3 | 2023-09-06 06:43:00 | 1
2023-2024 | INC-0060406 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Power disruption to site due to Storm Damage (disconnected power supply from Grid) | Type 3 | 2023-09-08 03:30:00 | 1
2023-2024 | INC-0060408 | Murray Bridge WWTP (Brinkley) | Heard load noise from the Inlet area of the Murray Bridge WWTP Brinkley, & noticed a dividing lid to the Inlet Screens had come loose & blown onto the ground due to very strong winds. | Type 3 | 2023-09-08 11:00:00 | 1
2023-2024 | INC-0060413 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2023-09-08 04:45:00 | 1
2023-2024 | INC-0060416 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): A/UV Effluent High Turbidity (>10 NTU) 6 hours due to Storms/High Rainfall Rainfall 07/09/2023 17.6mm Rainfall 08/09/2023 14.2mm | Type 2 | 2023-09-07 11:30:00 | 1
2023-2024 | INC-0060468 | Whyalla WWTP | Low water cap on lagoon 3 has in the past produced higher than normal odour levels. With the higher temperatures this weekend and light winds, we have a high possibility of higher odour levels being detected outside the plant. | Type 3 | 2023-09-15 12:30:00 | 1
2023-2024 | INC-0060492 | Port Augusta East WWTP | Contractor reported sewage leaking from excavated location at the Port Augusta East WWTP. Field Operations attended and confirmed. | Type 1 | 2023-09-19 06:45:00 | 1
2023-2024 | INC-0060511 | Port Lincoln WWTP | All 4 weirs faulted causing both basins to fault and shutdown processing . | Type 3 | 2023-09-20 10:14:00 | 1
2023-2024 | INC-0060577 | Port Lincoln WWTP | Reuse RTU Comms fault | Type 3 | 2023-09-27 08:52:00 | 1
2023-2024 | INC-0060612 | Port Lincoln WWTP | PLC had an error message on screen "Application MERuntime.exe encountered a serious error and must shut down" was the message . PLC Screen froze and had to restart. | Type 3 | 2023-09-29 10:08:00 | 1
2023-2024 | INC-0060634 | Whyalla WWTP | Had a storm event in during the night in Whyalla with strong winds with thunder and lightning. Approximately at 4am this morning the power had gone off for the WWTP. On call wasn't notified till 8am this morning about the event. | Type 3 | 2023-10-03 04:00:00 | 1
2023-2024 | INC-0060635 | Finger Point WWTP | call out from CC on Friday afternoon for weirs 1,2 & 3 position fault during decant. On arrival found decant 83% complete, weirs had all stopped travel, weir 1 at 9.71M, weir 2 at 9.70M and weir 3 at 9.71M (9.7M is 100% open). This fault typically appears if there has been a power outage/flick at the site. | Type 3 | 2023-09-29 15:30:00 | 1
2023-2024 | INC-0060651 | Finger Point WWTP | Four Finger Point aerators were refurbished in end RB16 and the new motors selected had a mild steel fan and cover (Lasted <5years). Several blades have been broken off the motor cooling fan and need replacing. Motor vibration sensors have all come off and will need refitting. Fan cover was sitting adjar on top of the aerator when the plant operator noticed it on site attendance today. | Type 3 | 2023-10-04 08:15:00 | 1
2023-2024 | INC-0060674 | Finger Point WWTP | The first diffuser section installed under the capital project was secured to the reef with chemical anchors and blocks. With recent seas that are regularly experienced in winter, this section has come adrift and noticed by the plant operator undertaking routine inspections. Tides and swell has not permitted safe inspection of the section of reef and what is still holding the piece in place but there is significant movement and the section could be lost before this occurs. | Type 3 | 2023-10-06 11:00:00 | 1
2023-2024 | INC-0060699 | Port Lincoln WWTP | Snake was sighted in rocks around polishing lagoon 1 whilst staff were walking around polishing lagoon during external EMS audit. | Type 3 | 2023-10-09 12:00:00 | 1
2023-2024 | INC-0060703 | Port Lincoln WWTP |  | Type 3 | 2023-10-10 12:12:00 | 1
2023-2024 | INC-0060712 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Higher than usual E.coli Effluent after UV SP42768 05/10/2023: 37 E.coli/100mL | Type 3 | 2023-10-05 07:45:00 | 1
2023-2024 | INC-0060713 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Free chlorine residual high, unable to see trend on SCADA Maximo job 09133380 | Type 3 | 2023-10-05 00:00:00 | 1
2023-2024 | INC-0060719 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | During importing of Mixed Liquor Suspended Solids (MLSS) to TFI WWTP for sludge seeding, approximately 50-100L of MLSS overflowed onto the slab and hardstand. Spill/material was contained within the site boundary. | Type 3 | 2023-10-11 10:30:00 | 1
2023-2024 | INC-0060735 | Port Lincoln WWTP |  | Type 3 | 2023-10-12 14:42:00 | 1
2023-2024 | INC-0060744 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | loss of aeration due to Mechanical failures on both rotors | Type 2 | 2023-10-13 11:30:00 | 1
2023-2024 | INC-0060767 | Port Lincoln WWTP |  | Type 3 | 2023-10-17 14:19:00 | 1
2023-2024 | INC-0060773 | Port Lincoln WWTP | weirs 1,2 & 3 faulted cause basin 1 to fault whilst in single basin operation | Type 3 | 2023-10-18 09:45:00 | 1
2023-2024 | INC-0060808 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Multiple SCADA alarms raised 3:30am this morning, approximately 1000L of treated wastewater overflowed from the aeration tank onto the concrete slab and surrounding concrete treated access road. Spill contained within SA Water WWTP site/boundary. | Type 3 | 2023-10-20 08:00:00 | 1
2023-2024 | INC-0060810 | Angaston WWTP | Leaking Imhoff effluent to lagoon 1, seepage across road for approximately 50m in direction of stormwater drainage, seepage noticed 24hrs prior, estimate approximately 10KL. | Type 2 | 2023-10-20 11:00:00 | 1
2023-2024 | INC-0060816 | Port Adelaide Sewer Relift Pump Station (PARPS) | Overflow chamber level went high, Hypo tank valve opened and pump started to run. 19-10-23 @ 16:04 Overflow tank level dropped and pump stopped running. Valve failed to close and a manual drain valve in the pipework was in the open position - not known. This left a flow path for the Hypo to drain the tank completely - Approximately 1,500 Litres into the bunded area. Not picked up until 7:00 on 20-10-23 | Type 2 | 2023-10-19 16:04:00 | 1
2023-2024 | INC-0060824 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Turbidity >10 NTU (>2 hours) | Type 2 | 2023-10-20 19:40:00 | 1
2023-2024 | INC-0060905 | Finger Point WWTP | Weir actuators are getting very old and faults are becoming more common. Weirs will stop until an operator has attended and can cause carry over of solids from the aeration basin and prevent the aerators to start the next cycle. | Type 3 | 2023-10-29 20:33:00 | 1
2023-2024 | INC-0060916 | Millicent WWTP | Distribution chamber receives sewage from the network and splits it into the four imhoff tanks. The chamber walls have been getting very thin, with aggregate in the concrete showing. It has been flagged to assets as needing a condition assessment. There does not appear to be a routine PM to check condition of structures at site. Should the distribution fail, the operators would not be aware until the site is visited and potential for sewage to run down the mound to the ground. Isolating this chamber would mean isolating the imhoff tanks and the primary treatment barrier. Reuse could also be impacted. | Type 3 | 2023-10-30 13:39:00 | 1
2023-2024 | INC-0060944 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): Low UV transmissivity (approx 23%), High Permeate Turbidity (>2 NTU) for greater than 1 hour | Type 1 | 2023-11-02 08:30:00 | 1
2023-2024 | INC-0060965 | Port Lincoln WWTP | Both RSPS became blocked and overflowed cake all over dewatering building floor. approx 4-5 ton had to be manually cleaned up. took two guy 4 hrs to tidy up. both guys experienced sore backs and arms next day. Wes Trotman OHS was onsite at the time. | Type 3 | 2023-11-01 11:41:00 | 1
2023-2024 | INC-0060969 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UVT on line measurement out of validation range for 5.5 hours due to blocked sample line | Type 3 | 2023-11-02 01:30:00 | 1
2023-2024 | INC-0060970 | Finger Point WWTP | As above | Type 3 | 2023-11-03 16:06:00 | 1
2023-2024 | INC-0061019 | Finger Point WWTP | Finger Point WWTP does not have a shed for the Tractor/Loader so rats are building in every place possible and bringing in straw material to build their nests. While plant assessor checks are completed by the operator it is not always possible to see where they have built nests or chewed through cables until started. Capital project to build an implement shed is constantly delayed and will likely be late next year before completion. Operator was within the main compound on this occasion but could potentially be in a high fire risk area when slashing. | Type 3 | 2023-11-09 11:00:00 | 1
2023-2024 | INC-0061024 | Bolivar High Salinity Waste Water Treatment Plant |  | Type 3 | 2023-11-10 13:59:00 | 1
2023-2024 | INC-0061081 | Murray Bridge WWTP (Brinkley) | Failure of the UV disinfection system, operations no longer able to discharge from site. External contractor required to repair system. | Type 2 | 2023-11-16 08:25:00 | 1
2023-2024 | INC-0061086 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): TARP: Anaerobic Digester: Manually venting Digester gas to atmosphere | Type 3 | 2023-11-16 12:30:00 | 1
2023-2024 | INC-0061093 | Finger Point WWTP | Position faults have been occurring when the decant weirs are operating (fail to lower, fail to raise) causing alarms and attendance by the operators every 4 hours to manually correct the issue. Failure to raise means the weirs are lowered, sending partially treated effluent over and out to the polishing lagoons and preventing the next aeration cycle to start. | Type 2 | 2023-11-11 13:30:00 | 1
2023-2024 | INC-0061116 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2023-2024 | INC-0061173 | Finger Point WWTP |  | Type 3 | 2023-11-22 09:00:00 | 1
2023-2024 | INC-0061182 | Murray Bridge WWTP (Brinkley) | complaint about the odour stench that she perceived to be coming from the WWTP yesterday. Reported to Stakeholder Engagement. was particularly strong in the early morning and late afternoons, quite strong odours more frequently and during any southerly wind directions | Type 3 | 2023-11-23 14:17:00 | 1
2023-2024 | INC-0061195 | Mount Burr WWTP | Additional pumping and/or network chokes are impacting Mt Burr WWTP due to capacity of downstream process/pipework limitations. Capital projects to upgrade pump station have resulted in greater capacity/higher flow rates than the WWTP can handle. | Type 3 | 2023-11-24 11:00:00 | 1
2023-2024 | INC-0061202 | Naracoorte WWTP (Treatment Works Rd) | High surface run off has flooded the sludge room. Approx 60mm rainfall today in 2 sort bursts has flooded the town and sent high flows above the capacity of the the WWTP. | Type 3 | 2023-11-24 19:50:00 | 1
2023-2024 | INC-0061203 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | Cape Jaffa power outage on the 24th but did not get the text through until the 25th. Aeration cycle part way through, so potential for first decant to have carry over of solids. | Type 3 | 2023-11-25 08:00:00 | 1
2023-2024 | INC-0061207 | Finger Point WWTP | Higher flows or longer pumping over the weekend has resulted in rag ball being brought into the inlet screen. Operator noted one a few weeks ago as well but not as bad as the one today. Material had been rolled up at the back of the screen, instead of going down the screw press and had got tangled up at the back of the step screen. There was also a lot of material that had accumulated in the inlet chamber that was just building up and had no where to go. Bypass had not yet been triggered. | Type 3 | 2023-11-27 06:30:00 | 1
2023-2024 | INC-0061208 | Millicent WWTP | No screen at Millicent WWTP to screen solids, so all solids coming into imhoff tanks are manually scooped off. | Type 3 | 2023-11-27 08:00:00 | 1
2023-2024 | INC-0061247 | Millicent WWTP | Millicent SPS1 has 2 pumps, however one was out for repairs when winter infiltration started earlier this year. The back up booster pump which was similar was installed as two pump operation was critical to minimise impacts to customers from surcharging and backing up in the network. However, now that flows have subsided, the temporary pump has a higher flow rate than normal when under one pump operation and the booster off. The WWTP has also been set to summer flows as Irrigation has started and short circuiting through the lagoons must be minimised to meet the Irrigation management plan. This has resulted in surcharging of the imhoff tanks when this pump is turned on (auto changes duty daily for 24hrs). | Type 3 | 2023-11-28 09:40:00 | 1
2023-2024 | INC-0061329 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): High oxygen demand load incident on Plant: Low Bioreactor A and C DOs | Type 3 | 2023-12-06 09:54:00 | 1
2023-2024 | INC-0061387 | Millicent WWTP | Farmer had purchased cattle the day prior. With storms overnight, the cattle jumped the fence and were wandering around the WWTP compound. Instead of contacting SAW, farmer cut the lock off and entered site, moved cattle and put another lock to which we had no key back on the gate to secure it. Plant operator attended site later in the day and found he was locked out from site. Farmer saw operator attending and let him know what he had done. | Type 3 | 2023-12-09 10:57:00 | 1
2023-2024 | INC-0061440 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Rotor 1a failure: Broken end plate/snapped shaft | Type 3 | 2023-12-15 09:56:00 | 1
2023-2024 | INC-0061445 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Blower 2 is out of service and Blower 1 is the only blower in service onsite with no back up. | Type 3 | 2023-12-15 10:00:00 | 1
2023-2024 | INC-0061535 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Ditch 1 Low pH | Type 3 | 2023-12-27 07:30:00 | 1
2023-2024 | INC-0061544 | Finger Point WWTP | Plant operator heard rumbling sound (built up gases) from the screen and investigated. Found the screen blocked with material and screw press choked. A lot of inert material has been coming into the plant over the last month and with power outages, the plant as a whole is struggling. Denitritrification performance has dropped off and chlorine demand over the weekend has changed, with fitters struggled to find optimum dosing ranges. Capital projects raised in multiple RBP's to address the screen safety issues and performance have not yet been delivered resulting in poor outcomes for our people (WHS notice only). Project has been raised again for RBP24 and safety of O&M must be made a priority in delivery of appropriate solution. | Type 3 | 2023-12-27 13:00:00 | 1
2023-2024 | INC-0061546 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Unusual loading/disinfection patterns | Type 3 | 2023-12-27 16:00:00 | 1
2023-2024 | INC-0061682 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2024-01-02 22:47:00 | 1
2023-2024 | INC-0061772 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Overflow of Storage due to lack of irrigation demand and fauklty level sensor | Type 1 | 2024-01-11 11:23:00 | 1
2023-2024 | INC-0061774 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2023-2024 | INC-0061778 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Brakes on the cage trailer TQO721 locked on during transit causing the drums to overheat and catch fire. Operator pulled over to a safe non grassed area and extinguished the fire with his vehicle fire extinguisher. | Type 3 | 2024-01-10 14:52:00 | 1
2023-2024 | INC-0061784 | Port Lincoln WWTP |  | Type 3 | 2024-01-06 17:30:00 | 1
2023-2024 | INC-0061785 | Port Lincoln WWTP |  | Type 3 | 2024-01-12 10:45:00 | 1
2023-2024 | INC-0061824 | Port Lincoln WWTP | High turbidity at the reuse plant. above 2.0 NTU for more than 1 hour | Type 2 | 2024-01-16 07:37:00 | 1
2023-2024 | INC-0061825 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Sewage Inlet: High Conductivity spikes (up to 10000 uS/cm) | Type 3 | 2024-01-16 08:00:00 | 1
2023-2024 | INC-0061880 | Normanville WWTP | Normanville WWTP Final Effluent A/C: SP93743: E.coli 400 cfu/100mL (F 1.3, T 2.0) 09/01/2024 | Type 2 | 2024-01-09 04:59:00 | 1
2023-2024 | INC-0061883 | Myponga Beach WWTP | Myponga Beach WWTP Irrigation Supply SP93746: Process overload verification sample | Type 3 | 2024-01-09 04:59:00 | 1
2023-2024 | INC-0061963 | Finger Point WWTP | New transformer installed in December seems to have different settings than the last one and an over current/surge event at 3am tripped the breaker. OCC called electrician who verified the outage was not due to SAW infrastructure. | Type 2 | 2024-01-24 03:00:00 | 1
2023-2024 | INC-0061981 | Finger Point WWTP |  | Type 3 | 2024-01-25 12:30:00 | 1
2023-2024 | INC-0062101 | Finger Point WWTP |  | Type 3 | 2024-02-05 04:00:00 | 1
2023-2024 | INC-0062181 | Christies Beach WWTP | Following a failure of the UV, the flow to C plant did not stop and <100kL of undisinfected effluent was discharged to the ocean. | Type 2 | 2024-02-08 17:50:00 | 1
2023-2024 | INC-0062212 | Heathfield WWTP | The building at Heathfield WWTP was originally a storage facility and has been modified into an office/ amenity. This has failed the BCA compliance audit. | Type 3 | 2024-02-12 14:53:00 | 1
2023-2024 | INC-0062221 | Naracoorte WWTP (Treatment Works Rd) | High levels of solids and grease from networks after rainfall events (3) continue to cause issues in downstream treatment streams. | Type 3 | 2024-02-13 11:00:00 | 1
2023-2024 | INC-0062230 | Normanville WWTP | Normanville WWTP: Hypochlorite dosing line split resulting in incomplete dosing into Chlorine Contact Tank (pipework) | Type 3 | 2024-02-14 09:00:00 | 1
2023-2024 | INC-0062440 | Victor Harbor (Boot) WWTP |  | Type 1 | 2024-02-29 14:05:00 | 1
2023-2024 | INC-0062484 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Effluent Turbidity >10NTU for 2.75 hours | Type 2 | 2024-03-02 12:00:00 | 1
2023-2024 | INC-0062486 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Turbidity >10 NTU for 6.75 hours | Type 2 | 2024-03-03 13:15:00 | 1
2023-2024 | INC-0062487 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Loss of aeration due to loss of SCADA signal | Type 1 | 2024-03-03 19:30:00 | 1
2023-2024 | INC-0062495 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Inlet pH below 6.5 on multiple days | Type 3 | 2024-03-05 08:00:00 | 1
2023-2024 | INC-0062528 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | No back up generator onsite or plug for temporary mobile generator for extended outages. UPS only on PLC. Notification of outage only received when site powered back up. | Type 3 | 2024-03-05 19:35:00 | 1
2023-2024 | INC-0062565 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carryover 4.25 hours, 101kL | Type 2 | 2024-03-13 04:00:00 | 1
2023-2024 | INC-0062576 | Naracoorte WWTP (Treatment Works Rd) |  | Type 3 | 2024-03-14 06:10:00 | 1
2023-2024 | INC-0062618 | Naracoorte WWTP (Treatment Works Rd) | Permit to work was signed/printed names of Field Ops teams. Previous similar incident at Millicent WWTP had notified teams of site steward. Contractor had keys and access card. | Type 3 | 2024-03-18 11:14:00 | 1
2023-2024 | INC-0062635 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Power outage, affecting whole Plant | Type 3 | 2024-03-20 09:45:00 | 1
2023-2024 | INC-0062675 | Finger Point WWTP | Electricians onsite were unable to start Aerator 5. Soft starter will need to be checked and replacement parts sought. Aerator will be offline until this is completed. | Type 3 | 2024-03-22 14:42:00 | 1
2023-2024 | INC-0062703 | Naracoorte WWTP (Treatment Works Rd) | We were investigating a recurring sewer odour complaint at Field Avenue Naracoorte WO 09469516 & found that further downstream two Educt Vents were blocked ID 2367527 & ID 2367529 | Type 3 | 2024-03-21 11:00:00 | 1
2023-2024 | INC-0062813 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): UV system operating just above cutoff limits | Type 3 | 2024-04-08 07:30:00 | 1
2023-2024 | INC-0062882 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Turbidity >10NTU 7.25 hours | Type 2 | 2024-04-13 12:35:00 | 1
2023-2024 | INC-0062917 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Turbidity of Effluent discharge to Creek >10NTU for 4.5 hours | Type 2 | 2024-04-16 09:45:00 | 1
2023-2024 | INC-0062918 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Turbidity of Effluent discharge to Creek >10NTU for 1.5 hours | Type 3 | 2024-04-17 14:50:00 | 1
2023-2024 | INC-0062936 | Finger Point WWTP | The material looks like a liner or coating and is too big to typically fit down a toilet and pass through the screen. | Type 3 | 2024-04-19 14:57:00 | 1
2023-2024 | INC-0062941 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Denitrification caused solids to carry over. May have been caused by lack of aeration during maintenance activities | Type 2 | 2024-04-18 18:30:00 | 1
2023-2024 | INC-0062946 | Normanville WWTP | Pipe work between Chlorine pump and Storage IBC failed causing about 900Lts of hypo to leak into the bunded containment area. No hypo left this bunded area as it was ALL contained in the underground tank. | Type 3 | 2024-04-21 08:00:00 | 1
2023-2024 | INC-0062947 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Poly returned to bio-reactor causing over flocculation of MLSS. | Type 3 | 2024-04-21 16:00:00 | 1
2023-2024 | INC-0062953 | Finger Point WWTP | Electricians called out to see if they could identify the issue (potentially switchgear - no spares). Aerator 5 has had the same fault for a few weeks and cause has also not been identified. | Type 3 | 2024-04-20 01:45:00 | 1
2023-2024 | INC-0063002 | Finger Point WWTP | Operator reported that they had difficulties on Friday and now again today with the screw press not working. The stringy material coming into the plant is far greater that what the inlet screen can handle and is not the right equipment for the job. Operations has been awaiting delivery of a Capital project with an improved solution for many years (new screening plant around the end of pumping main the preferred option). | Type 3 | 2024-04-29 13:36:00 | 1
2023-2024 | INC-0063051 | Angaston WWTP | Angaston Lagoon WWTP (Stockwell Rd): Irrigation without disinfection for approx 4.75 hours, then 2.5 hours | Type 3 | 2024-05-03 13:42:00 | 1
2023-2024 | INC-0063067 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): A/C Effluent Turbidity >10 NTU 13 hours | Type 2 | 2024-05-03 14:20:00 | 1
2023-2024 | INC-0063068 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): A/C Effluent Turbidity >10 NTU 15 hours | Type 2 | 2024-05-04 16:15:00 | 1
2023-2024 | INC-0063069 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): A/C Effluent Turbidity >10 NTU 10 hours | Type 2 | 2024-05-05 15:15:00 | 1
2023-2024 | INC-0063077 | Victor Harbor (Boot) WWTP |  | Type 1 | 2024-03-06 08:00:00 | 1
2023-2024 | INC-0063082 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Something has blocked the Supernatant PS to cause it to overflow approve. 10 - 20 kL on site and it flowed outside the WWTP gate. It has pooled in the salt flats around the WWTP. | Type 2 | 2024-05-07 08:26:00 | 1
2023-2024 | INC-0063111 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 5.5 hours, 172kL | Type 2 | 2024-05-07 22:25:00 | 1
2023-2024 | INC-0063112 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 6 hours, 244kL | Type 2 | 2024-05-08 15:56:00 | 1
2023-2024 | INC-0063113 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 6.75 hours, 229kL | Type 2 | 2024-05-08 16:15:00 | 1
2023-2024 | INC-0063153 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 7.75 hours, 301kL | Type 2 | 2024-05-10 06:50:00 | 1
2023-2024 | INC-0063154 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 7.5 hours, 320kL | Type 2 | 2024-05-11 15:00:00 | 1
2023-2024 | INC-0063155 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10 NTU 9.75 hours, 302kL | Type 2 | 2024-05-12 17:00:00 | 1
2023-2024 | INC-0063173 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Effluent Manhole SP4883: 29/04/2024 Suspended Solids 22 mg/L | Type 3 | 2024-04-29 12:00:00 | 1
2023-2024 | INC-0063175 | Finger Point WWTP | rag ball rolling up in bottom of step screen had built up and jammed, blocking the inlet to the screen preventing any further rag removal from influent | Type 3 | 2024-05-13 14:00:00 | 1
2023-2024 | INC-0063213 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2023-2024 | INC-0063220 | Finger Point WWTP | Generator onsite for chlorine started automatically. Site generator not yet connected. | Type 3 | 2024-05-20 07:00:00 | 1
2023-2024 | INC-0063276 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | We had a power outage on Friday afternoon at Port Pirie WWTP which wasn't noticed until Monday morning when the operator rocked up to site. The RAS UPS Power Supply Fault alarm had triggered but on call operator wasn't informed. The result was there was no aeration occurring for over two days, the plant overflowed solids into Lagoon 3A and the inlet valve for SBR 1 had failed. The inlet screens had overflowed a small amount of sewage onto site that did not leave site. | Type 3 | 2024-05-20 15:47:00 | 1
2023-2024 | INC-0063342 | Port Lincoln WWTP | Drill rig being used in abandoned sludge lagoon 4 in WWTP burst a hydraulic hose and discharged approx 10 litres of hydraulic oil on ground | Type 3 | 2024-05-23 15:45:00 | 1
2023-2024 | INC-0063350 | Angaston WWTP | Front left hand tyre popped when driving east along Angaston Rd just past bridge | Type 3 | 2024-05-27 10:20:00 | 1
2023-2024 | INC-0063352 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Effluent turbidity >10 NTU 4 hours, 160 kL | Type 2 | 2024-05-24 11:20:00 | 1
2023-2024 | INC-0063353 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Effluent turbidity >10 NTU 7 hours, 267 kL | Type 2 | 2024-05-24 13:30:00 | 1
2023-2024 | INC-0063354 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Effluent turbidity >10 NTU 11.5 hours, 511 kL | Type 2 | 2024-05-25 11:45:00 | 1
2023-2024 | INC-0063355 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Effluent turbidity >10 NTU 8 hours, 330 kL | Type 2 | 2024-05-26 14:20:00 | 1
2023-2024 | INC-0063525 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10NTU 7.5 hours, 330kL | Type 2 | 2024-06-01 12:15:00 | 1
2023-2024 | INC-0063526 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10NTU 6.25 hours, 237kL: Multi factor Plant operational instabilities | Type 2 | 2024-06-05 19:50:00 | 1
2023-2024 | INC-0063527 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >10NTU 12.25 hours, 501kL: Multi factor Plant operational instabilities | Type 2 | 2024-06-06 13:15:00 | 1
2023-2024 | INC-0063533 | Finger Point WWTP | Intermittent inlet screen system faults have been occurring since Thursday when operators are onsite. These have been able to be reset. PLC is to be replaced as part of delayed capital project as it is redundant. | Type 3 | 2024-06-08 00:25:00 | 1
2023-2024 | INC-0063548 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carry over, Turbidity >10NTU: 11 hours, 446kL | Type 2 | 2024-06-08 13:45:00 | 1
2023-2024 | INC-0063549 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carry over, Turbidity >10NTU: 10.25 hours, 434kL | Type 2 | 2024-06-09 13:20:00 | 1
2023-2024 | INC-0063583 | Angaston WWTP | Angaston Lagoon WWTP (Stockwell Rd): Creek Discharge 14kL, Lagoon levels >105% | Type 2 | 2024-05-27 12:00:00 | 1
2023-2024 | INC-0063585 | Angaston WWTP | Angaston Lagoon WWTP (Stockwell Rd): Creek discharge 15kL | Type 1 | 2024-04-26 18:00:00 | 1
2023-2024 | INC-0063600 | Christies Beach WWTP | At 4.17pm on the 14/6/24 UV bankC22 had an adjacent lamp failure fault that did not trigger a shutdown of the bank and thus did not alarm. This resulted in flow going through the UV until 6.56am 15/6/24 when the operator attended site in the morning. The UV dose for the whole period was above 80mJ/cm2 for the duration of the event in that train. | Type 2 | 2024-06-15 07:07:00 | 1
2023-2024 | INC-0063669 | Finger Point WWTP | ragbag had rolled up inside step screen until it was jammed, blocking inlet to screw press, bypassing influent into aeration lagoon | Type 3 | 2024-06-24 08:06:00 | 1
2023-2024 | INC-0063676 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carry over, Turbidity >10NTU: 8.25 hours, 651kL | Type 2 | 2024-06-14 11:20:00 | 1
2023-2024 | INC-0063726 | Finger Point WWTP | Plant operator was nearby with maintenance team as wash water for the screen has had electrical faults and is not working well. | Type 3 | 2024-06-28 13:42:00 | 1
2023-2024 | INC-0063732 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | Contractor doing switchboard upgrades at Leigh Creek didn't inform operations that they were shutting down the aerators on site over the weekend (24/5 to 27/5) to conduct switchboard upgrades. Our EPA Licence agreement states that we are required to have aeration on at all times. It was reported to SA Water after the fact. | Type 3 | 2024-05-31 12:00:00 | 1
2023-2024 | INC-0063754 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carry over, Turbidity >10NTU: 9.5 hours, 892kL | Type 2 | 2024-06-29 09:25:00 | 1
2024-2025 | INC-0063755 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): Solids carry over, Turbidity >10NTU: 1.25 hours, 1329kL | Type 3 | 2024-07-01 01:00:00 | 1
2024-2025 | INC-0063763 | Heathfield WWTP | Blower 2 VSD fault, VSD showing "input phase loss", | Type 3 | 2024-07-02 10:00:00 | 1
2024-2025 | INC-0063773 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2024-2025 | INC-0063774 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): SP 4555 E.coli 390 orgs/100mL | Type 3 | 2024-07-02 04:59:00 | 1
2024-2025 | INC-0063781 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): High (24 hour average) Turbidity in Post Membrane effluent due to air entrainment | Type 3 | 2024-07-04 10:41:00 | 1
2024-2025 | INC-0063897 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): SP4555 AC Effluent High ammonia since May 2024 | Type 3 | 2024-07-17 10:40:00 | 1
2024-2025 | INC-0063933 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Power flick interrupted alum dosing pump operations, resulting in higher than normal turbidity in AC Effluent | Type 3 | 2024-07-20 05:45:00 | 1
2024-2025 | INC-0063956 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity outflow >10NTU 1.0 hour, 55kL | Type 3 | 2024-07-25 06:50:00 | 1
2024-2025 | INC-0063987 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carry over, Turbidity >10NTU: 22.5 hours, 1206kL | Type 2 | 2024-07-27 11:00:00 | 1
2024-2025 | INC-0064044 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) | No remote connection could affect alarm notifications from plant. Trending of water tank levels indicate Telstra may not have an outage, as first thought. | Type 3 | 2024-08-04 09:37:00 | 1
2024-2025 | INC-0064050 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Chlorine dosing system: Trip of Emergency Shutdown (chlorine dose stopped for 2.5 hours) | Type 1 | 2024-08-05 11:20:00 | 1
2024-2025 | INC-0064071 | Murray Bridge WWTP (Brinkley) | The treated excess water discharged to the on-site swale is now flooding back to the plant and entering the supernatant pump station. The additional water is distorting the chemical dosing and therefore interrupting the treatment process. We are now in a treatment loop as the excess water on-site is increasing every day and increasing the size of the problem. | Type 2 | 2024-08-08 13:10:00 | 1
2024-2025 | INC-0064107 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Mixed Liquor: Cessation of nitrification | Type 3 | 2024-08-01 00:00:00 | 1
2024-2025 | INC-0064132 | Naracoorte WWTP (Treatment Works Rd) | Primary pump station overflowed for several hours into the front paddock (approx 900kL) | Type 1 | 2024-08-19 08:58:00 | 1
2024-2025 | INC-0064134 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carrying over Clarifiers, Turbidity >20 NTU 3.5 hours, 224kL | Type 2 | 2024-08-16 01:20:00 | 1
2024-2025 | INC-0064135 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carrying over Clarifiers, Turbidity >20 NTU 2.0 hours, 108kL | Type 2 | 2024-08-16 11:32:00 | 1
2024-2025 | INC-0064136 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carrying over Clarifiers, Turbidity >20 NTU 3.0 hours, 182kL | Type 2 | 2024-08-16 23:40:00 | 1
2024-2025 | INC-0064137 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carrying over Clarifiers, Turbidity >20 NTU 12 hours, 851kL | Type 2 | 2024-08-17 14:30:00 | 1
2024-2025 | INC-0064138 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Solids carrying over Clarifiers, Turbidity >20 NTU 8.25 hours, 561kL | Type 2 | 2024-08-18 16:20:00 | 1
2024-2025 | INC-0064145 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): Loss of SCADA control of Plant | Type 3 | 2024-08-20 08:00:00 | 1
2024-2025 | INC-0064154 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Event, Solids Carryover: Turb >20 NTU 0.75hr, 28kL, >10NTU 4.25hr, 177kl | Type 3 | 2024-08-20 01:50:00 | 1
2024-2025 | INC-0064155 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Event, Solids Carryover: Turb >20 NTU 0.1hr, 8kL, >10NTU 0.75hr, 80kL: High inflow due to high recent rainfall ... Switching of Aeration in Ditch 1 due to Maintenance activities | Type 3 | 2024-08-20 10:50:00 | 1
2024-2025 | INC-0064156 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Event, Solids Carryover: Turb >20 NTU 1.25, 86kL, >10NTU 4.25hr, 236kL: High inflow due to high recent rainfall ... Switching of Aeration in Ditch 1 due to Maintenance activities | Type 3 | 2024-08-20 22:00:00 | 1
2024-2025 | INC-0064162 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | Noticeable odour coming from Port Pirie WWTP, potentially from desludging operations occurring on Sludge Lagoon 1. Operator reported seeing comments on social media regarding 'bad smells blowing across town from the sewage plant lately'. Other site visitors noted odour was noticeable on the way up to the plant. | Type 3 | 2024-08-21 08:00:00 | 1
2024-2025 | INC-0064167 | Heathfield WWTP | Sludge lagoon is nearly full and in danger of overflowing due to no operational pumps available. | Type 3 | 2024-08-22 13:01:00 | 1
2024-2025 | INC-0064235 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2024-09-02 10:15:00 | 1
2024-2025 | INC-0064237 | Mount Burr WWTP |  | Type 3 | 2024-09-02 08:00:00 | 1
2024-2025 | INC-0064242 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): High winds keeping Aeration Basin mixed ... carry over of solids into Polishing Lagoons | Type 3 | 2024-09-02 12:00:00 | 1
2024-2025 | INC-0064246 | Murray Bridge WWTP (Brinkley) | Operator notified Coordinator and Manager of multiple blower failures. Currently running Blower #1 in manual with no back-up/contingency available. Logged jobs with Murray Bridge Workshops. #2, reported to be awaiting part #3, failed | Type 3 | 2024-09-03 06:50:00 | 1
2024-2025 | INC-0064330 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Aeration Basin: High turbidity/Suspended Solids in Decanted Effluent due to Storm activity mixing Basin contents (during Settle, Decant) | Type 3 | 2024-09-04 12:00:00 | 1
2024-2025 | INC-0064332 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Aeration Basin: High turbidity/Suspended Solids in Decanted Effluent due to Storm activity mixing Basin contents (during Settle, Decant) | Type 3 | 2024-09-11 12:00:00 | 1
2024-2025 | INC-0064365 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP Brinkley experiencing loss of communication to SCADA. This freezes the SCADA screen & in turn the OCC have no signs of anything wrong or see any faults to the plant. Operators have no real time visual & have no control over the plant onsite or remotely. | Type 2 | 2024-09-16 06:15:00 | 1
2024-2025 | INC-0064369 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Ditch #1, Rotor #1a: Rotor #1a failure | Type 3 | 2024-09-09 11:00:00 | 1
2024-2025 | INC-0064378 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Alum dosing: Split dosing line immediately post alum pumps resulted in approx 300 litres of alum being directed to the alum area bund | Type 3 | 2024-09-16 13:00:00 | 1
2024-2025 | INC-0064416 | Murray Bridge WWTP (Brinkley) | Plant unable to treat & process as per required. | Type 1 | 2024-09-20 06:15:00 | 1
2024-2025 | INC-0064431 | Finger Point WWTP | Inlet screens were offline a few weeks ago to facilitate maintenance works. Likely unscreened material in the basin (over time) has accumulated in sludge wasting line. Sludge wasting isolation valve and MLR valves are currently seized or broken. | Type 3 | 2024-09-23 10:09:00 | 1
2024-2025 | INC-0064432 | Millicent WWTP | No automatic screen at Millicent WWTP. Manual bar screen (100mm) for very large rag balls retrofitted but difficult to clean. | Type 3 | 2024-09-23 12:36:00 | 1
2024-2025 | INC-0064444 | Port Augusta West WWTP | Got a call from OCC reporting a fault on the chlorine dosing. Logged on and checked SCADA, found that chlorine dose reading and flow meter reading in fault and not reading correctly. Asked occ to contact on-call CL2 fitter to investigate issue. | Type 3 | 2024-09-24 01:00:00 | 1
2024-2025 | INC-0064464 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | A sewer overflow was discovered by the Maintenance team (operator on leave) during a site visit to complete repairs at the Pirie Wastewater Treatment Plant (WWTP). It was determined that the plant's PLC had been switched off the day before at 15:45 and did not resume operation when powered back on. As a result, all communications from the plant were frozen from 15:45 on the 24th until the PLC was restarted at 10:35 on the 25th. Aside from a minor overflow caused by blocked screens and high water levels in the "Online" basin, the plant was not significantly impacted, and it came back online without issue. Alarms were triggered by the PLC, but at the same time, a PLC alarm for Whyalla Water Reclamation Plant (WRP) also appeared. We later discovered that both alarms are connected to the same alert for unknown reasons. Due to ongoing work on the alarm systems (SCADA team re-enabling some previously disabled alarm areas), we initially assumed the Whyalla alarm was related to this work. Upon investigating the Whyalla issue on the 24th, we found its PLC to be functioning correctly. Based on this, we assumed the alarm was linked to the system changes and deferred further investigation until the following morning. This is why we missed the legitimate Pirie alarm | Type 3 | 2024-09-25 10:00:00 | 1
2024-2025 | INC-0064467 | Normanville WWTP | Normanville WWTP: Chlorine residual analyser: Unstable operation not enabling automatic chlorine residual control | Type 3 | 2024-09-27 07:30:00 | 1
2024-2025 | INC-0064513 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP Brinkley SCADA for plant freezing resulting in Operators & OCC having NO control of plant, having NO real time visual of plant & NO ability of resetting alarms/faults. | Type 2 | 2024-10-03 06:24:00 | 1
2024-2025 | INC-0064554 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV transmissivity meter reading 20.2% due to dirty cell: When cleaned, reading reverted to >50% | Type 3 | 2024-08-21 08:08:00 | 1
2024-2025 | INC-0064555 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV transmissivity meter reading 20.2% due to dirty cell: When cleaned, reading reverted to >50% | Type 3 | 2024-08-30 07:11:00 | 1
2024-2025 | INC-0064596 | Mount Burr WWTP | Approve 50L sewer overflow 7 Gray St Mount burr W09774448 . was reported previous day as a leaking valve | Type 3 | 2024-10-10 14:47:00 | 1
2024-2025 | INC-0064620 | Heathfield WWTP | Power flick through Heathfield WWTP, blowers faulting on over temp or over pressure, Blowers 1, 3, 4 all have broken belts to various degrees, | Type 2 | 2024-10-16 01:00:00 | 1
2024-2025 | INC-0064647 | Naracoorte WWTP (Treatment Works Rd) | High rainfall in short period of time at Naracoorte causing high flows via gravity mains into WWTP. One pump has been out for approx 2years and Primary pump station is part wany through capital project to refurbish mech and elec. The capital project will not address the hydraulic/treatment issues experienced at the plant. EIP investigation has been started. | Type 2 | 2024-10-18 09:09:00 | 1
2024-2025 | INC-0064649 | Finger Point WWTP | Capital project to be delivered in RD24 to address flooding issues. | Type 3 | 2024-10-18 07:15:00 | 1
2024-2025 | INC-0064650 | Port Pirie Activated Sludge WWTP (Kitchener Tce) | The WWTP was bypassed at 930pm 17/10/24 due to significant power outage in town, flow was averaged at +80l/s overnight. - Potential loss of treatment in efficiency in the coming months. - Potential for odour from the WWTP due to high temperatures in the coming weeks and the water being in the sludge lagoon. Will work through to get the water back through the WWTP once the power is restored. Expecting issues with process at Activated Sludge plant when power is restored. UPS was connected to genset at 1130pm to maintain comms with WWTP and Pirie Sewer Network Current ETA on power return is 2pm 18/10. | Type 3 | 2024-10-18 08:00:00 | 1
2024-2025 | INC-0064658 | Leigh Creek Wastewater Treatment Plant (Aerating Lagoons) | • Power and communications were lost to the wider far northern region of SA (Stirling North to Lyndhurst) on Thursday evening as a result of the sever storm that moved through the area. • Power and communications have not been restored to Leigh Creek at this time and expected to be early next week until generation can be put in place and connected into the network. • High volume of rainfall occurred in the area • Until SA Water can confirm the occurrence of any overflow from Lagoon 3, we are assuming this occurred, as previously observed in 2021/22 during similar storms. | Type 3 | 2024-10-18 08:00:00 | 1
2024-2025 | INC-0064761 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Brown snake spotted hiding in rocks neck to access gate | Type 3 | 2024-10-30 10:49:00 | 1
2024-2025 | INC-0064767 | Port Augusta West WWTP | Chlorine drums were isolated onsite since 24/10 and 3.9ML of undisinfected water was irrigated at the Port Augusta Golf Course from the 24/10 until 29/10. The low chlorine alarm was active and not operator disabled but was not triggered. Irrigation times from flow meter and confirmed with Golf Course: Thursday night: midnight - 09:12am Friday night: 20:30 to 02:35am Saturday night: no irrigation Sunday night: midnight - 06:47am Monday night: 20:34 to 07:14am Tuesday night: 20:30 to 2:30am | Type 1 | 2024-10-30 13:11:00 | 1
2024-2025 | INC-0064770 | Millicent WWTP | Imhoff tanks were unable to be deragged this week as planned as birds nests had caused Vermeer unit to fail. There is no shed at Milicent WWTP suitable to park very expensive truck out of the weather/away from vermin. This has been on OIR for some time. | Type 3 | 2024-10-28 09:22:00 | 1
2024-2025 | INC-0064773 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV transmissivity meter: Measured UVT <35% for 3.75 hours, 364kL: Presumed to be a dirty UVT meter cell | Type 3 | 2024-10-31 10:00:00 | 1
2024-2025 | INC-0064815 | Point Pearce WWTP (Parrys Av) | Operator and TPO attended Point Pearce WWTP site and observed that the sludge tank had overflowed approximately 100L of sludge with approx. 5 L leaking through the site fence onto the neighbouring property. | Type 2 | 2024-11-06 10:00:00 | 1
2024-2025 | INC-0064937 | Point Pearce WWTP (Parrys Av) | Workshops noticed the overflow going into the Emergency Lagoon while onsite yesterday afternoon. A volume of 30kL (worst case, based on inflows) has discharged into the Emergency Lagoon (Bamboo Forest) at Point Pearce WWTP. The reason for the overflow is because of contract works for a plant upgrade occurring onsite, we have no ability to irrigate and normal operation of the WWTP is to irrigate 100% of the recycled water with no discharge to the environment. We have organised Minalton Septic to come out each day to remove as much as they can from the aeration and decant tanks, but due to an emergency call out for them, and limited availability, they were unable to attend yesterday. The contracts are planned to be onsite until Thursday 21/11/24. | Type 2 | 2024-11-14 16:00:00 | 1
2024-2025 | INC-0064982 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2024-2025 | INC-0064996 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Ditch 1 DO: Lower than normal DO in Ditch 1 for week 18/11 to 25/11 | Type 3 | 2024-11-25 14:00:00 | 1
2024-2025 | INC-0065106 | Normanville WWTP | Normanville WWTP: SBR#2 Inlet Valve Actuator Failure | Type 3 | 2024-12-03 05:38:00 | 1
2024-2025 | INC-0065148 | Port Lincoln WWTP | All 4 weirs faulted (encoder) causing basins to fault. operator intervention is required to correct basins | Type 3 | 2024-12-10 14:28:00 | 1
2024-2025 | INC-0065162 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV disinfection system: Lower UVT and UV dose than usual due to higher flows post pigging | Type 3 | 2024-12-11 15:58:00 | 1
2024-2025 | INC-0065199 | Finger Point WWTP | rag ball became wedged in step screen chute, overloading motor resulting in influent bypassing screen direct into aeration basin for 1 hour | Type 3 | 2024-12-13 20:10:00 | 1
2024-2025 | INC-0065224 | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd) | Bird In Hand Activated Sludge WWTP (Bird In Hand Rd): Bioreactor High MLSS | Type 3 | 2024-12-18 14:21:00 | 1
2024-2025 | INC-0065228 | Finger Point WWTP | Finger Point Activated Sludge WWTP (Hutt Bay Rd): Polishing Lagoons: Declining Performance | Type 3 | 2024-12-18 15:28:00 | 1
2024-2025 | INC-0065231 | Nangwarry WWTP | abnormally high inflows to Nangwarry no 1 SPS led to a high imhoff tank level alarm at the WWTP. Suspect discharge into sewer system, possibly from town swimming pool? | Type 3 | 2024-12-18 09:30:00 | 1
2024-2025 | INC-0065259 | Heathfield WWTP | An automatic fire alarm was triggered in the aeration blower room at the Heathfield WWTP. Smoke was seen to be escaping from the room through the door seals, all operators onsite vacated the immediate area and entered the control room to monitor the blower operation and wait for the CFS to arrive. CFS arrived and with BA sets on entered the room, it was declared safe although there was a heavy smell of burnt electrical cables. | Type 2 | 2024-12-19 15:44:00 | 1
2024-2025 | INC-0065276 | Port Lincoln WWTP | Grit and Screens high high level alarm. Upon investigation had noticed water on the ground and found the Grit and Screens inlet channel had overflowed. at the time step screen was operating and the manual screen was clear. approx 20ltrs on the ground . also wet ragging was event on the outside of the structure. by the time i went to have a look, level had dropped itself. | Type 3 | 2024-12-23 08:50:00 | 1
2024-2025 | INC-0065302 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): Aeration Tank: Overaeration due to low Plant loading resulted in foam overflow from Aeration Tank(s) | Type 3 | 2024-12-27 07:30:00 | 1
2024-2025 | INC-0065303 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Oxidation Ditches: Overaeration due to continual operation of Portable/Supplemental Aeration/Aspirators (high nitrate) | Type 3 | 2024-12-30 14:00:00 | 1
2024-2025 | INC-0065386 | Finger Point WWTP | Operator found a large rag ball in the Inlet Screen that had broken off some of the spray nozzles. | Type 3 | 2025-01-03 12:26:00 | 1
2024-2025 | INC-0065413 | Port Lincoln WWTP | All 4 weirs faulted causing Aeration basin faults and process implications. operation need to intervene to correct process | Type 3 | 2025-01-09 11:29:00 | 1
2024-2025 | INC-0065462 | Bolivar Wastewater Treatment Plant |  |  |  | 1
2024-2025 | INC-0065499 | Finger Point WWTP | Electrical switchboard upgrade capital project has still not been completed (~5yrs), so onsite generator is unable to support basic plant function. Small generator at chlorine building providing some dosing of partially treated wastewater at this stage. SAPN text suggest power may be restored by 2pm. Screen is offline, so bypass will be activated when it becomes blocked. Operator noted there was also a power flick on Sunday around 730am also. Oncall person was not notified as potentially short outage. | Type 3 | 2025-01-20 07:30:00 | 1
2024-2025 | INC-0065550 | Port Lincoln WWTP | Half of UV lamps (30 out of 60) were tripped at Port Lincoln Reuse Plant. A T1 incident occurs when we have seven or more UV lamps out for more than one hour. The reuse plant was running between 16:53 and 17:41 on the 21/01/25 and again from 23:32 on the 21/01/25 until 07:00 on the 22/01/25 where the operator shut down the plant. Council were reusing the water during these periods of time. UVT has flatling on SCADA and chlorine residual was around the 2 mg/L and turbidity was around 0.5 NTU. | Type 1 | 2025-01-22 07:00:00 | 1
2024-2025 | INC-0065575 | Finger Point WWTP | rag had balled up on the inlet to the step screen, blocking the channel to the screw press | Type 3 | 2025-01-26 08:30:00 | 1
2024-2025 | INC-0065583 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV Transmissivity: Effluent Post Storage: <35% for 4 hours 20 minutes | Type 3 | 2024-12-18 04:09:00 | 1
2024-2025 | INC-0065584 | Murray Bridge WWTP (Brinkley) |  | Type 3 | 2024-12-19 01:28:00 | 1
2024-2025 | INC-0065629 | Millicent WWTP | ragball in splitter box blocked inlet screen and inlet to imhoff tank | Type 3 | 2025-01-29 12:00:00 | 1
2024-2025 | INC-0065686 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): 01/02/2025 Type 2 High turbidity Effluent >20 NTU: 3 hours, 123 kL | Type 3 | 2025-02-01 18:20:00 | 1
2024-2025 | INC-0065687 | Port Lincoln WWTP | All 4 weirs faulted causing both basins to fault | Type 3 | 2025-02-04 03:13:00 | 1
2024-2025 | INC-0065710 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 6.5 hours, 213 kL | Type 2 | 2025-02-05 21:55:00 | 1
2024-2025 | INC-0065721 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): 06/02/2025 INC-0065686 Type 2 High turbidity Effluent >20 NTU: >20 NTU: 2.5 hours, 78 kL | Type 2 | 2025-02-06 12:45:00 | 1
2024-2025 | INC-0065723 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): 06/02/2025 High turbidity Effluent >20 NTU: 9.5 hours, 342 kL (Time and volume exacerbated by blocked sample filter) | Type 2 | 2025-02-06 17:20:00 | 1
2024-2025 | INC-0065724 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): High turbidity post membranes | Type 3 | 2025-02-07 11:00:00 | 1
2024-2025 | INC-0065736 | Port Lincoln WWTP | Grit classifier auger motor gearbox faulted during operation. Was noted as being noisy the day prior and then stopped working and could not be reset | Type 3 | 2025-02-09 02:35:00 | 1
2024-2025 | INC-0065737 | Port Lincoln WWTP | Both digested sludge bio-gas water heaters went into fault and could not be reset | Type 3 | 2025-02-09 16:45:00 | 1
2024-2025 | INC-0065746 | Port Lincoln WWTP | Carry out controlled digester gas release due to bio-gas water heaters being offline. | Type 3 | 2025-02-10 18:50:00 | 1
2024-2025 | INC-0065767 | Port Lincoln WWTP | Manual bio gas release is required due to Bio gas heaters failure | Type 3 | 2025-02-12 07:26:00 | 1
2024-2025 | INC-0065773 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 2.5 hours, 113 kL | Type 2 | 2025-02-09 19:20:00 | 1
2024-2025 | INC-0065801 | Port Lincoln WWTP | Carry out the controlled release of digester bio-gas due to bio-gas hot water heater package being offline. | Type 3 | 2025-02-12 19:00:00 | 1
2024-2025 | INC-0065917 | Finger Point WWTP | rag ball was rolling up on inlet to step screen, influent level rose and was bypassing direct into aeration basin | Type 3 | 2025-02-18 13:00:00 | 1
2024-2025 | INC-0065934 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 1.5 hours, 79 kL | Type 3 | 2025-02-18 23:00:00 | 1
2024-2025 | INC-0065969 | Port Lincoln WWTP | Control room called for low chlorine alarm. when plant was checked there was no low alarm present. there is a very long delay in information being sent causing false alarms. the delay of information turned into a RTU comms fault which continued on for 40 minutes | Type 3 | 2025-02-21 14:20:00 | 1
2024-2025 | INC-0066051 | Finger Point WWTP | different teams using bore water at the same time resulted in loss of pressure and flow leaving dredging contractor with insufficient water in balance tank to continue filtering operations | Type 3 | 2025-02-26 10:00:00 | 1
2024-2025 | INC-0066059 | Finger Point WWTP | civil contractors on site were filling a water tanker and bore could not maintain sufficient supply to dredging contractors balance water tank to keep plant running. | Type 3 | 2025-02-28 11:31:00 | 1
2024-2025 | INC-0066107 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 5.5 hours, 213 kL | Type 2 | 2025-03-03 16:00:00 | 1
2024-2025 | INC-0066148 | Finger Point WWTP | during routine mechanical maintenance fitters found the rubber buffer mooring block on the Northern central mooring line had failed. All buffer blocks (12) are at least 18 months past due replacement date (blocks are no longer available). | Type 3 | 2025-03-06 12:00:00 | 1
2024-2025 | INC-0066149 | Point Pearce WWTP (Parrys Av) | Remote Communities engineer attended the Point Pearce WWTP and observed that the sludge holding tank had overflowed - approximately 100L of sludge. Does not appear to have flowed outside boundary. | Type 2 | 2025-03-07 11:59:00 | 1
2024-2025 | INC-0066158 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 3.5 hours, 143 kL | Type 2 | 2025-03-05 21:00:00 | 1
2024-2025 | INC-0066159 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 14.0 hours, 475 kL | Type 2 | 2025-03-07 14:30:00 | 1
2024-2025 | INC-0066168 | Mount Burr WWTP |  | Type 3 | 2025-03-11 07:30:00 | 1
2024-2025 | INC-0066172 | Nangwarry WWTP |  | Type 3 | 2025-03-11 07:30:00 | 1
2024-2025 | INC-0066174 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): UV transmissivity sensor faulting | Type 3 | 2025-03-08 12:00:00 | 1
2024-2025 | INC-0066178 | Port Lincoln WWTP | Risk of not meeting TARP requirements for site if we have a failure of either our one online RDT or one online RSP. RSP 1 has been offline since 25/11/24. Operators submitted a Service Request to get pump, non-return valve and flow meter replaced. RDT poly pumps for both trains were offline today and we had to steal parts from another train to get one train working (RDT 2 is online). The issue was both pumps weren't working. There was also a broken solenoid valve in the bottom tank of Thickening poly which was diluting the poly and causing thickness issues with the digester. As we only have one RDT and one RSP online, we are vulnerable if we have either go out on fault or breakdown. | Type 3 | 2025-03-11 13:00:00 | 1
2024-2025 | INC-0066212 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 2.0 hours, 58 kL | Type 2 | 2025-03-11 22:50:00 | 1
2024-2025 | INC-0066239 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Intermittent power failures affecting Inlet Works | Type 3 | 2025-03-13 01:55:00 | 1
2024-2025 | INC-0066258 | Port Augusta Prison WWTP | Blocked pipe that caused an overflow on the 27/02/2025 until the 06/03/2025. One odour complaint has come through. | Type 3 | 2025-03-14 11:52:00 | 1
2024-2025 | INC-0066268 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 12.5 hours, 374 kL | Type 2 | 2025-03-13 19:00:00 | 1
2024-2025 | INC-0066282 | Finger Point WWTP | Risk assessment identified outage as high risk. Mitigation strategy was to have a back up generator onsite for such occasion as generator was new and had not been run previously and outage was 7 days and could not be reversed in a failure. Emergency service plans were to also be in place. | Type 3 | 2025-03-09 01:00:00 | 1
2024-2025 | INC-0066329 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 10.5 hours, 265 kL | Type 2 | 2025-03-17 21:00:00 | 1
2024-2025 | INC-0066330 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 125 hours, 455 kL | Type 2 | 2025-03-18 16:00:00 | 1
2024-2025 | INC-0066346 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 20.5 hours, 757 kL | Type 2 | 2025-03-19 15:00:00 | 1
2024-2025 | INC-0066361 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 10.5 hours, 338 kL | Type 2 | 2025-03-20 06:15:00 | 1
2024-2025 | INC-0066363 | Port Lincoln WWTP |  | Type 3 | 2025-03-21 14:33:00 | 1
2024-2025 | INC-0066377 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 13.75 hours, 433 kL | Type 2 | 2025-03-21 21:15:00 | 1
2024-2025 | INC-0066378 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 11.5 hours, 467 kL | Type 2 | 2025-03-22 13:50:00 | 1
2024-2025 | INC-0066380 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 2.5 hours, 78 kL | Type 2 | 2025-03-23 22:45:00 | 1
2024-2025 | INC-0066394 | Glenelg Waste Water Treatment Plant | 8 dead birds identified on D plant clarifiers, this is an unusual number of birds to be found at this location. | Type 3 | 2025-03-25 13:50:00 | 1
2024-2025 | INC-0066395 | Whyalla WWTP | Effluent is potentially leaking from Lagoon 5/6 on the eastern side of Horseshoe Road into the mudflats north of the discharge channel and east of the Lagoon 5/6. The volume of water pooling in the mud flats is considerable, especially since there have been no high or king tides or significant rainfall that would contribute to the water being present. | Type 3 | 2025-03-24 09:40:00 | 1
2024-2025 | INC-0066397 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 2.5 hours, 76 kL | Type 2 | 2025-03-24 22:45:00 | 1
2024-2025 | INC-0066404 | Finger Point WWTP | swan drowned after weir decant effluent trapped bird against mesh screen(approx 10 swans and 30 ducks or waterfowl killed per year) | Type 3 | 2025-03-25 06:45:00 | 1
2024-2025 | INC-0066472 | Point Pearce WWTP (Parrys Av) | Due to ongoing T1 Health incident (high E.coli), we have been unable to irrigate and subsequently backed up the process to the decant tank where we discharged approx. 10kL of effluent to the Emergency Lagoon (Bamboo Forest) via the overflow of the decant tank. The discharge began at 11:33AM on the 30/03/25 and continued for 21.5 hours until 09:00AM on the 31/103/25. A second discharge occurred for 24 hours from 09:45AM on 01/04/2025 until 09:45AM on the 02/04/2025 and discharged approx. 10 kL. | Type 2 | 2025-03-31 08:00:00 | 1
2024-2025 | INC-0066479 | Port Lincoln WWTP | Raw feed pump to re-use plant low flow alarm caused by blocked inlet screen by horsehair algae. Re-use plant would not run. Clearing of the inlet screen required manual raking of external area around inlet chamber before screen could be lifted. Lifting of inlet screen is very heavy and awkward when blocked with horsehair algae and could lead to injury if not carried out with due care. | Type 3 | 2025-03-30 06:00:00 | 1
2024-2025 | INC-0066484 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 5 hours, 197 kL | Type 2 | 2025-03-30 19:15:00 | 1
2024-2025 | INC-0066505 | Pallamana Wastewater Treatment Plant (Wilkin Rd) | Pallamana Wastewater Treatment Plant (Wilkin Rd): Sewage SP458801: Unusual sewage characteristics | Type 3 | 2025-03-12 00:00:00 | 1
2024-2025 | INC-0066512 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 12.5 hours, 574 kL | Type 2 | 2025-04-01 11:30:00 | 1
2024-2025 | INC-0066524 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 11.5 hours, 475 kL | Type 2 | 2025-04-02 13:30:00 | 1
2024-2025 | INC-0066555 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 1.5 hours, 27 kL | Type 3 | 2025-04-05 21:00:00 | 1
2024-2025 | INC-0066556 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 5 hours, 208 kL | Type 2 | 2025-04-06 19:00:00 | 1
2024-2025 | INC-0066562 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd):High turbidity Effluent >20 NTU: 6.0 hours, 179kL | Type 2 | 2025-04-07 21:15:00 | 1
2024-2025 | INC-0066595 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Process carry water line, PVC pipework was broken during removal of tree roots with excavator. The pipe work was laid against buried tree root | Type 3 | 2025-04-08 13:06:00 | 1
2024-2025 | INC-0066607 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 6.0 hours, 366L | Type 2 | 2025-04-08 17:00:00 | 1
2024-2025 | INC-0066613 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 9.5 hours, 385kL | Type 2 | 2025-04-09 16:00:00 | 1
2024-2025 | INC-0066623 | Victor Harbor (Boot) WWTP |  | Type 3 | 2025-04-10 11:05:00 | 1
2024-2025 | INC-0066632 | Murray Bridge WWTP (Brinkley) | Circuit breaker inside solar switchboard cabinet has failed. Resulting in multiple CB's melting and becoming unserviceable. | Type 3 | 2025-03-14 14:46:00 | 1
2024-2025 | INC-0066648 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): Load quantification for Solids Carryover events | Type 3 | 2025-04-11 00:00:00 | 1
2024-2025 | INC-0066649 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 12.25 hours, 472kL | Type 2 | 2025-04-10 14:50:00 | 1
2024-2025 | INC-0066680 | Port Lincoln WWTP | Mains supply of potable water for use in the sludge handling process is affected when extraction from the network close to the site occurs. The network pressure is not sufficient to supply the process and causes a carry water low flow alarm which shuts down processing. | Type 3 | 2025-04-15 09:50:00 | 1
2024-2025 | INC-0066696 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 6 hours, 223kL | Type 2 | 2025-04-12 18:55:00 | 1
2024-2025 | INC-0066698 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 7 hours, 211kL | Type 2 | 2025-04-15 20:10:00 | 1
2024-2025 | INC-0066699 | Heathfield WWTP | Heathfield Activated Sludge WWTP (Brick Kiln Rd): A/UV Effluent >1.0 mg/L Total Phosphorus | Type 3 | 2025-04-03 04:59:00 | 1
2024-2025 | INC-0066712 | Port Augusta West WWTP | The chlorine analyser and chlorine drum 2 are not communicating either on site or on SCADA so we have no visibility of the chlorine residual. This first occurred at 3:45am on the 17/04/25 and is currently still not visible. | Type 2 | 2025-04-17 12:00:00 | 1
2024-2025 | INC-0066758 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 10hours, 346kL | Type 2 | 2025-04-16 17:45:00 | 1
2024-2025 | INC-0066759 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 5 hours, 176kL | Type 2 | 2025-04-17 11:30:00 | 1
2024-2025 | INC-0066760 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 13.75 hours, 336kL | Type 2 | 2025-04-17 19:25:00 | 1
2024-2025 | INC-0066761 | Hahndorf Activated Sludge WWTP (Ambleside Rd) | Hahndorf Activated Sludge WWTP (Ambleside Rd): High turbidity Effluent >20 NTU: 8.75 hours, 347kL | Type 2 | 2025-04-19 17:15:00 | 1
2024-2025 | INC-0066790 | Finger Point WWTP |  | Type 3 | 2025-04-21 11:40:00 | 1
2024-2025 | INC-0066821 | Whyalla WWTP | A dredging contractor lightly contacted an aerator cable that was electrically isolated, resulting in a minor surface nick. The aerator and electrical cable was prior to works commencing. The aerator was relocated alongside the bank to reduce impact to the dredging team, however part of the cable remained submerged within the lagoon. The dredge operator reported an alarm on the barge indicating something blocked within the auger, this was found to be the aerator cable. Dredge operator removed the cable from the auger and placed on the float of the aerator for inspection. TPO attended site to confirm impact. Dredging contractor completed incident report (attached). | Type 2 | 2025-04-28 14:50:00 | 1
2024-2025 | INC-0066845 | Cape Jaffa Wastewater Treatment Plant (Seafarer Pde) |  | Type 3 | 2025-04-29 14:01:00 | 1
2024-2025 | INC-0066855 | Murray Bridge WWTP (Brinkley) | Murray Bridge WWTP (Brinkley): Polymer system failure which in turn affected Clarifier operations, resulting in high SS effluent | Type 2 | 2025-04-30 08:00:00 | 1
2024-2025 | INC-0066927 | Mount Burr WWTP | Mount Burr Lagoon WWTP (Thomas Dr): Polishing Lagoon Effluent: High BOD, SS | Type 3 | 2025-04-14 11:15:00 | 1
Grand Total | [5 empty] | 924